## Raw data
Data | influent flow Q m3/d | % RAS | return activated sludge rate Qr m3/d | % WAS | Waste activated sludge rate Qw m3/d | mixed liquor suspended solids MLSS (mg/L) | SV 30 (mL/L) | sludge volume index SVI (ml/g) | Dissolved Oxygen DO mg/l | temperature T | sludge blanket m | total suspended solid TSS in mg/l | total suspended solid TSS out mg/l | Chemical Oxygen Demand COD in mg/l | Chemical Oxygen Demand COD out mg/l | Biochemical Oxygen Demand BOD in mg/l | Biochemical Oxygen Demand BOD out mg/l | PH
2025-01-01 | 11273 | 60 | 6763.8 | 3.5 | 394.555 | 1815 | 174 | 95.8678 | 2.8 | 18.9 | 0.67 | 140 | 11 | 350 | 34.3 | 250 | 10 | 7.2
2025-01-02 | 11273 | 60 | 6763.8 | 3.5 | 394.555 | 1830 | 179 | 97.8142 | 2.5 | 19.2 | 0.29 | 130 | 10 | 432 | 27 | 248 | 7.8 | 7.15
2025-01-03 | 11298 | 60 | 6778.8 | 3.5 | 395.43 | 1829 | 161 | 88.0262 | 2.94 | 18.5 | 0.44 | 134 | 7.3 | 400 | 28.5 | 253 | 6 | 7.24
2025-01-04 | 11312 | 60 | 6787.2 | 3.4 | 384.608 | 1819 | 183 | 100.6047 | 3.1 | 19 | 0.41 | 150 | 13.5 | 500 | 42 | 251 | 10 | 7.21
2025-01-05 | 11286 | 60 | 6771.6 | 3.4 | 383.724 | 1814 | 190 | 104.7409 | 1.2 | 17 | 0.73 | 155 | 14 | 341 | 32 | 246 | 9.5 | 7.2
2025-01-06 | 11294 | 60 | 6776.4 | 3.6 | 406.584 | 1833 | 159 | 86.743 | 3.2 | 19.3 | 0.7 | 160 | 7 | 432 | 21 | 150 | 6 | 7.25
2025-01-07 | 11385 | 60 | 6831 | 3.3 | 375.705 | 1827 | 177 | 96.8801 | 2.9 | 18.6 | 0.83 | 118 | 10 | 400 | 31.6 | 249 | 8.7 | 7.19
2025-01-08 | 11410 | 60 | 6846 | 3.5 | 399.35 | 1837 | 188 | 102.3408 | 6 | 19 | 0.32 | 144 | 13 | 500 | 36.1 | 252 | 10 | 7.22
2025-01-09 | 11686 | 60 | 7011.6 | 3.6 | 420.696 | 1833 | 189 | 103.1097 | 3 | 16 | 0.54 | 154 | 13.5 | 520 | 38 | 300 | 10.3 | 7.2
2025-01-10 | 11606 | 60 | 6963.6 | 3.6 | 417.816 | 1837 | 166 | 90.3647 | 2.7 | 19 | 0.29 | 170 | 9 | 540 | 26 | 250 | 8 | 7.23
2025-01-11 | 11598 | 60 | 6958.8 | 3.4 | 394.332 | 1842 | 167 | 90.6623 | 3.15 | 18 | 0.41 | 135 | 7.6 | 440 | 30 | 168 | 7 | 7.2
2025-01-12 | 11599 | 60 | 6959.4 | 3.3 | 382.767 | 1812 | 171 | 94.3709 | 2.6 | 19 | 0.59 | 121 | 8.9 | 400 | 32 | 245 | 7.6 | 7.16
2025-01-13 | 11731 | 60 | 7038.6 | 3.5 | 410.585 | 1843 | 168 | 91.1557 | 2.9 | 18.7 | 0.29 | 167 | 8.7 | 430 | 28.8 | 140 | 6 | 7.24
2025-01-14 | 11683 | 60 | 7009.8 | 3.5 | 408.905 | 1820 | 191 | 104.9451 | 2.4 | 19.3 | 0.4 | 160 | 13.5 | 350 | 42.2 | 248 | 10.2 | 7.19
2025-01-15 | 11856 | 60 | 7113.6 | 3.5 | 414.96 | 1805 | 182 | 100.831 | 6 | 18 | 0.68 | 164 | 13 | 460 | 39 | 310 | 10 | 7.22
2025-01-16 | 11808 | 60 | 7084.8 | 3.4 | 401.472 | 1805 | 171 | 94.7368 | 2.8 | 17 | 0.61 | 137 | 9 | 490 | 26.1 | 246 | 8 | 7.2
2025-01-17 | 11848 | 60 | 7108.8 | 3.4 | 402.832 | 1810 | 187 | 103.3149 | 3 | 18 | 0.41 | 168 | 15 | 500 | 43 | 254 | 9.8 | 7.23
2025-01-18 | 11869 | 58 | 6884.02 | 3.6 | 427.284 | 1839 | 176 | 95.7042 | 2.5 | 16 | 0.64 | 132 | 11 | 430 | 30 | 300 | 8.4 | 7.7
2025-01-19 | 11858 | 58 | 6877.64 | 3.6 | 426.888 | 1815 | 183 | 100.8264 | 2.9 | 18 | 0.78 | 131 | 13 | 500 | 40 | 247 | 8 | 7.65
2025-01-20 | 11844 | 58 | 6869.52 | 3.4 | 402.696 | 1811 | 156 | 86.1403 | 2.3 | 18.3 | 0.27 | 120 | 6.5 | 400 | 24 | 253 | 6.2 | 7.74
2025-01-21 | 11791 | 58 | 6838.78 | 3.3 | 389.103 | 1840 | 190 | 103.2609 | 2.15 | 17.5 | 0.78 | 122 | 12 | 533 | 34.5 | 300 | 8 | 7.7
2025-01-22 | 11770 | 58 | 6826.6 | 3.5 | 411.95 | 1826 | 193 | 105.6955 | 2.42 | 18 | 0.71 | 125.5 | 12.5 | 530 | 34 | 260 | 9.9 | 7.72
2025-01-23 | 11822 | 58 | 6856.76 | 3.4 | 401.948 | 1814 | 167 | 92.0617 | 2.3 | 18 | 0.48 | 160 | 7.1 | 530 | 30 | 252 | 6.8 | 7.66
2025-01-24 | 11780 | 58 | 6832.4 | 3.4 | 400.52 | 1836 | 183 | 99.6732 | 1 | 18 | 0.37 | 125 | 10 | 490 | 31 | 246 | 6.7 | 7.75
2025-01-25 | 11797 | 58 | 6842.26 | 3.6 | 424.692 | 1809 | 159 | 87.8939 | 2.2 | 16 | 0.87 | 124 | 7 | 500 | 23.6 | 100 | 6.4 | 7.69
2025-01-26 | 11823 | 58 | 6857.34 | 3.3 | 390.159 | 1836 | 174 | 94.7712 | 2.45 | 17 | 0.48 | 118 | 9 | 540 | 27.9 | 152 | 7 | 7.7
2025-01-27 | 11924 | 58 | 6915.92 | 3.5 | 417.34 | 1816 | 170 | 93.6123 | 2.3 | 19 | 0.33 | 127 | 9 | 455 | 31 | 249 | 7.6 | 7.67
2025-01-28 | 11919 | 58 | 6913.02 | 3.6 | 429.084 | 1836 | 186 | 101.3072 | 7 | 18.4 | 0.33 | 160 | 12 | 460 | 36 | 251 | 8.7 | 7.73
2025-01-29 | 11923 | 58 | 6915.34 | 3.6 | 429.228 | 1830 | 166 | 90.7104 | 2.2 | 18 | 0.8 | 165 | 9 | 432 | 30.7 | 247 | 7 | 7.7
2025-01-30 | 12045 | 58 | 6986.1 | 3.4 | 409.53 | 1831 | 179 | 97.7608 | 2.4 | 18.6 | 0.65 | 120 | 9 | 550 | 31 | 253 | 6.8 | 7.74
2025-01-31 | 10625 | 58 | 6162.5 | 3.4 | 361.25 | 1781 | 193 | 108.3661 | 2.35 | 17 | 0.78 | 130 | 12 | 500 | 42.9 | 248 | 9 | 7.69
2025-02-01 | 9750 | 58 | 5655 | 3.4 | 331.5 | 1774 | 176 | 99.2108 | 2.2 | 17 | 0.73 | 125 | 12 | 500 | 33.7 | 252 | 9 | 7.72
2025-02-02 | 15041 | 58 | 8723.78 | 3.6 | 541.476 | 1806 | 189 | 104.6512 | 2.48 | 17.5 | 0.61 | 158 | 14 | 523 | 37 | 246 | 10 | 7.7
2025-02-03 | 15084 | 58 | 8748.72 | 3.3 | 497.772 | 1800 | 171 | 95 | 2.3 | 18 | 0.88 | 128 | 9 | 470 | 26.3 | 110 | 6.7 | 7.75
2025-02-04 | 15122 | 58 | 8770.76 | 3.5 | 529.27 | 1784 | 194 | 108.7444 | 2.5 | 18.5 | 0.51 | 138 | 13 | 370 | 39 | 249 | 9.4 | 7.5
2025-02-05 | 15665 | 58 | 9085.7 | 3.6 | 563.94 | 1796 | 187 | 104.1203 | 7 | 18 | 0.62 | 133 | 12 | 470 | 39.2 | 254 | 10 | 7.45
2025-02-06 | 15710 | 58 | 9111.8 | 3.6 | 565.56 | 1805 | 197 | 109.1413 | 2.4 | 17 | 0.79 | 180 | 13.4 | 520 | 37.6 | 247 | 9 | 7.52
2025-02-07 | 16287 | 58 | 9446.46 | 3.4 | 553.758 | 1791 | 199 | 111.1111 | 2.3 | 19 | 0.66 | 200 | 16 | 556 | 40.2 | 250 | 10.3 | 7.46
2025-02-08 | 16372 | 58 | 9495.76 | 3.6 | 589.392 | 1779 | 184 | 103.4289 | 2.45 | 18 | 0.81 | 180 | 13.2 | 530 | 34.6 | 253 | 9.4 | 7.5
2025-02-09 | 16641 | 58 | 9651.78 | 3.3 | 549.153 | 1786 | 180 | 100.7839 | 2.9 | 16 | 0.63 | 176 | 12 | 470 | 38 | 245 | 9.5 | 7.44
2025-02-10 | 16675 | 58 | 9671.5 | 3.5 | 583.625 | 1783 | 180 | 100.9534 | 3.15 | 17 | 0.71 | 170 | 12 | 450 | 37.8 | 251 | 8.6 | 7.51
2025-02-11 | 16406 | 58 | 9515.48 | 3.6 | 590.616 | 1800 | 163 | 90.5556 | 2.72 | 16 | 0.3 | 155 | 9.2 | 480 | 32 | 248 | 7.2 | 7.47
2025-02-12 | 16462 | 58 | 9547.96 | 3.6 | 592.632 | 1770 | 164 | 92.6554 | 3 | 17 | 0.41 | 140 | 9.5 | 500 | 27.8 | 252 | 7.9 | 7.5
2025-02-13 | 16373 | 58 | 9496.34 | 3.4 | 556.682 | 1787 | 197 | 110.2406 | 2.8 | 16 | 0.45 | 189 | 16 | 460 | 44 | 246 | 9.9 | 7.45
2025-02-14 | 16373 | 58 | 9496.34 | 3.3 | 540.309 | 1700 | 171 | 100.5882 | 3.2 | 17 | 0.32 | 190 | 13 | 500 | 37.6 | 254 | 8.1 | 7.52
2025-02-15 | 16175 | 58 | 9381.5 | 3.5 | 566.125 | 1796 | 172 | 95.7684 | 2.85 | 16 | 0.42 | 140 | 9.5 | 450 | 31 | 250 | 8.9 | 7.46
2025-02-16 | 16212 | 58 | 9402.96 | 3.5 | 567.42 | 1785 | 192 | 107.563 | 3.1 | 16 | 0.33 | 132 | 14 | 430 | 42.3 | 247 | 11 | 7.5
2025-02-17 | 16047 | 58 | 9307.26 | 3.5 | 561.645 | 1781 | 202 | 113.4194 | 2.9 | 17 | 0.45 | 136 | 12 | 470 | 36 | 253 | 9 | 7.43
2025-02-18 | 16061 | 58 | 9315.38 | 3.4 | 546.074 | 1770 | 160 | 90.3955 | 3.12 | 18 | 0.67 | 133 | 9 | 390 | 32 | 251 | 8 | 7.51
2025-02-19 | 15781 | 58 | 9152.98 | 3.4 | 536.554 | 1789 | 192 | 107.3225 | 2.7 | 18 | 0.5 | 127 | 10 | 496 | 31.4 | 248 | 7.7 | 7.47
2025-02-20 | 15795 | 58 | 9161.1 | 3.6 | 568.62 | 1702 | 170 | 99.8825 | 3 | 17 | 0.5 | 150 | 10 | 530 | 32 | 168 | 7 | 7.5
2025-02-21 | 15710 | 58 | 9111.8 | 3.6 | 565.56 | 1807 | 187 | 103.4864 | 2.84 | 16 | 0.4 | 190 | 15 | 544 | 43 | 246 | 11 | 7.46
2025-02-22 | 15682 | 58 | 9095.56 | 3.4 | 533.188 | 1781 | 173 | 97.1364 | 3.2 | 17 | 0.44 | 147 | 7.2 | 480 | 20.4 | 250 | 6 | 7.3
2025-02-23 | 15436 | 58 | 8952.88 | 3.6 | 555.696 | 1783 | 189 | 106.0011 | 2.7 | 16.5 | 0.86 | 186 | 14 | 490 | 38 | 254 | 9.7 | 7.26
2025-02-24 | 15498 | 58 | 8988.84 | 3.6 | 557.928 | 1807 | 175 | 96.8456 | 5 | 17 | 0.68 | 123 | 11 | 444 | 32 | 249 | 7 | 7.34
2025-02-25 | 15157 | 58 | 8791.06 | 3.4 | 515.338 | 1803 | 170 | 94.2873 | 2.92 | 16.7 | 0.65 | 175 | 10 | 443 | 28.9 | 251 | 7 | 7.3
2025-02-26 | 10050 | 58 | 5829 | 3.3 | 331.65 | 1795 | 177 | 98.6072 | 2.9 | 16 | 0.38 | 140 | 12 | 447 | 34.2 | 247 | 8 | 7.32
2025-02-27 | 15031 | 58 | 8717.98 | 3.5 | 526.085 | 1795 | 171 | 95.2646 | 2.8 | 17 | 0.73 | 127 | 11 | 449 | 38.5 | 253 | 9 | 7.27
2025-02-28 | 15049 | 58 | 8728.42 | 3.5 | 526.715 | 1775 | 191 | 107.6056 | 3.05 | 19 | 0.37 | 157 | 9 | 438 | 26.1 | 248 | 8.6 | 7.35
2025-03-01 | 14937 | 58 | 8663.46 | 3.5 | 522.795 | 1802 | 181 | 100.444 | 3 | 18 | 0.51 | 150 | 12 | 445 | 38.7 | 252 | 9 | 7.29
2025-03-02 | 14948 | 58 | 8669.84 | 3.4 | 508.232 | 1937 | 195 | 100.6711 | 6 | 18 | 0.89 | 130 | 12 | 429 | 29.2 | 246 | 7.8 | 7.3
2025-03-03 | 15049 | 58 | 8728.42 | 3.4 | 511.666 | 1944 | 192 | 98.7654 | 2.85 | 19 | 0.67 | 143 | 10 | 435 | 30 | 251 | 8 | 7.27
2025-03-04 | 14937 | 58 | 8663.46 | 3.6 | 537.732 | 1926 | 203 | 105.3998 | 3.2 | 16 | 0.62 | 150 | 13 | 445 | 38 | 249 | 9 | 7.33
2025-03-05 | 14948 | 58 | 8669.84 | 3.6 | 538.128 | 1932 | 181 | 93.6853 | 3 | 16 | 0.7 | 165 | 8.6 | 438 | 30.5 | 254 | 8.5 | 7.3
2025-03-06 | 15084 | 58 | 8748.72 | 3.4 | 512.856 | 1921 | 195 | 101.5096 | 3.52 | 17 | 0.8 | 144 | 12 | 500 | 37.7 | 247 | 6.9 | 7.32
2025-03-07 | 15498 | 58 | 8988.84 | 3.3 | 511.434 | 2030 | 200 | 98.5222 | 2.9 | 18 | 0.76 | 1135 | 9.3 | 452 | 33 | 250 | 8 | 7.26
2025-03-08 | 15157 | 58 | 8791.06 | 3.5 | 530.495 | 1919 | 200 | 104.2209 | 3.3 | 16.7 | 0.41 | 200 | 14 | 439 | 37.9 | 253 | 8.9 | 7.34
2025-03-09 | 15710 | 58 | 9111.8 | 3.4 | 534.14 | 1952 | 208 | 106.5574 | 3.1 | 16.4 | 0.29 | 200 | 14.5 | 443 | 38.5 | 245 | 8.4 | 7.3
2025-03-10 | 16287 | 58 | 9446.46 | 3.4 | 553.758 | 1948 | 183 | 93.9425 | 3.44 | 17 | 0.47 | 150 | 7.8 | 430 | 29.9 | 251 | 7.2 | 7.33
2025-03-11 | 16372 | 58 | 9495.76 | 3.6 | 589.392 | 1916 | 176 | 91.858 | 2.8 | 16 | 0.52 | 130 | 7.5 | 454 | 25 | 248 | 7 | 7.7
2025-03-12 | 15710 | 58 | 9111.8 | 3.3 | 518.43 | 1937 | 193 | 99.6386 | 3.3 | 16.8 | 0.4 | 161 | 10 | 447 | 27 | 252 | 6.8 | 7.64
2025-03-13 | 16287 | 58 | 9446.46 | 3.5 | 570.045 | 1943 | 207 | 106.5363 | 2.95 | 16 | 0.86 | 153 | 13 | 540 | 33 | 246 | 8.7 | 7.73
2025-03-14 | 16372 | 58 | 9495.76 | 3.6 | 589.392 | 1920 | 177 | 92.1875 | 1.2 | 16.7 | 0.82 | 145 | 7 | 540 | 21.9 | 254 | 6.2 | 7.7
2025-03-15 | 16675 | 58 | 9671.5 | 3.5 | 583.625 | 1934 | 176 | 91.0031 | 4 | 16.5 | 0.47 | 155 | 9 | 540 | 31 | 250 | 7 | 7.72
2025-03-16 | 16406 | 58 | 9515.48 | 3.4 | 557.804 | 1947 | 195 | 100.1541 | 3.8 | 16.8 | 0.68 | 135 | 13.3 | 540 | 38 | 247 | 9 | 7.66
2025-03-17 | 16462 | 58 | 9547.96 | 3.4 | 559.708 | 1942 | 173 | 89.0834 | 4.24 | 17 | 0.52 | 160 | 8 | 530 | 30 | 253 | 6.6 | 7.75
2025-03-18 | 16373 | 58 | 9496.34 | 3.6 | 589.428 | 1915 | 202 | 105.483 | 3.9 | 18 | 0.85 | 140 | 13.3 | 490 | 36 | 251 | 10 | 7.69
2025-03-19 | 16373 | 58 | 9496.34 | 3.6 | 589.428 | 1955 | 194 | 99.2327 | 4.1 | 18.4 | 0.56 | 150 | 12 | 540 | 35.8 | 248 | 10 | 7.7
2025-03-20 | 16407 | 58 | 9516.06 | 3.4 | 557.838 | 1928 | 197 | 102.1784 | 3.75 | 17 | 0.44 | 154 | 12 | 500 | 37 | 252 | 8.5 | 7.65
2025-03-21 | 16409 | 58 | 9517.22 | 3.6 | 590.724 | 1942 | 176 | 90.6282 | 4.2 | 18 | 0.43 | 136 | 8 | 400 | 26.1 | 246 | 6 | 7.74
2025-03-22 | 16337 | 58 | 9475.46 | 3.6 | 588.132 | 1920 | 187 | 97.3958 | 3.9 | 18 | 0.62 | 160 | 10.5 | 490 | 33.8 | 250 | 7.1 | 7.7
2025-03-23 | 16248 | 58 | 9423.84 | 3.4 | 552.432 | 1924 | 179 | 93.0353 | 4.1 | 19 | 0.44 | 153 | 8.9 | 550 | 27 | 254 | 7.9 | 7.72
2025-03-24 | 16171 | 58 | 9379.18 | 3.3 | 533.643 | 1943 | 179 | 92.1256 | 3.84 | 17 | 0.64 | 153 | 9 | 500 | 28 | 249 | 8 | 7.66
2025-03-25 | 15671 | 58 | 9089.18 | 3.5 | 548.485 | 1946 | 183 | 94.0391 | 4.2 | 18 | 0.84 | 164 | 7.8 | 400 | 25.4 | 251 | 6.1 | 7.73
2025-03-26 | 15296 | 58 | 8871.68 | 3.5 | 535.36 | 1921 | 185 | 96.304 | 3.9 | 18 | 0.52 | 153 | 11.5 | 370 | 30 | 247 | 8.3 | 7.7
2025-03-27 | 15122 | 58 | 8770.76 | 3.4 | 514.148 | 1940 | 197 | 101.5464 | 4.05 | 18 | 0.41 | 145 | 12 | 450 | 36.9 | 253 | 9.3 | 7.71
2025-03-28 | 14921 | 58 | 8654.18 | 3.4 | 507.314 | 2202 | 200 | 90.8265 | 4.2 | 17.6 | 0.9 | 155 | 8 | 540 | 26 | 248 | 7.4 | 7.67
2025-03-29 | 14832 | 58 | 8602.56 | 3.6 | 533.952 | 1936 | 169 | 87.2934 | 3.8 | 18.5 | 0.59 | 146.4 | 6.5 | 470 | 24.2 | 252 | 6.1 | 7.5
2025-03-30 | 14498 | 58 | 8408.84 | 3.3 | 478.434 | 1917 | 180 | 93.8967 | 5 | 18 | 0.33 | 144 | 10 | 540 | 33 | 246 | 8.4 | 7.46
2025-03-31 | 13796 | 58 | 8001.68 | 3.5 | 482.86 | 1920 | 168 | 87.5 | 3.92 | 18.4 | 0.3 | 126 | 6 | 500 | 25 | 251 | 5.5 | 7.54
2025-04-01 | 13461 | 58 | 7807.38 | 3.6 | 484.596 | 1994 | 198 | 99.2979 | 4.1 | 21 | 0.34 | 140 | 9.5 | 351 | 33 | 249 | 7.2 | 7.5
2025-04-02 | 13165 | 58 | 7635.7 | 3.6 | 473.94 | 2014 | 189 | 93.8431 | 3.9 | 20 | 0.67 | 135 | 9 | 344 | 28.8 | 254 | 7.5 | 7.52
2025-04-03 | 12666 | 58 | 7346.28 | 3.4 | 430.644 | 1997 | 199 | 99.6495 | 4.05 | 24 | 0.77 | 162 | 10.9 | 344 | 31 | 247 | 9 | 7.47
2025-04-04 | 12707 | 58 | 7370.06 | 3.3 | 419.331 | 2029 | 198 | 97.585 | 5 | 23.8 | 0.54 | 150 | 9 | 352 | 28.9 | 250 | 8 | 7.55
2025-04-05 | 12623 | 58 | 7321.34 | 3.5 | 441.805 | 1998 | 178 | 89.0891 | 4.8 | 24 | 0.31 | 144 | 8 | 336 | 21 | 253 | 6.3 | 7.49
2025-04-06 | 12543 | 58 | 7274.94 | 3.5 | 439.005 | 2430 | 209 | 86.0082 | 5.14 | 22 | 0.51 | 124 | 7 | 327 | 20 | 245 | 6.4 | 7.5
2025-04-07 | 12460 | 58 | 7226.8 | 3.5 | 436.1 | 2028 | 206 | 101.5779 | 4.9 | 20 | 0.9 | 168 | 13 | 345 | 32 | 251 | 8 | 7.48
2025-04-08 | 12414 | 58 | 7200.12 | 3.4 | 422.076 | 1999 | 199 | 99.5498 | 4.7 | 23 | 0.6 | 150 | 9.9 | 327 | 27.4 | 248 | 7 | 7.53
2025-04-09 | 12300 | 63 | 7749 | 3.6 | 442.8 | 2000 | 190 | 95 | 3 | 22 | 0.7 | 170 | 13 | 400 | 28 | 250 | 10 | 7
2025-04-10 | 12296 | 58 | 7131.68 | 3.6 | 442.656 | 2003 | 189 | 94.3585 | 4.85 | 23.6 | 0.81 | 123 | 10 | 330 | 28 | 246 | 8 | 7.5
2025-04-11 | 12145 | 58 | 7044.1 | 3.3 | 400.785 | 2029 | 189 | 93.1493 | 5.1 | 22 | 0.28 | 185 | 14 | 440 | 37.8 | 254 | 10 | 7.46
2025-04-12 | 12168 | 58 | 7057.44 | 3.5 | 425.88 | 2016 | 212 | 105.1587 | 5 | 20 | 0.72 | 200 | 16 | 555 | 47.8 | 250 | 9.9 | 7.54
2025-04-13 | 11918 | 58 | 6912.44 | 3.6 | 429.048 | 2024 | 201 | 99.3083 | 5.04 | 21 | 0.7 | 146 | 8.9 | 325 | 27.7 | 247 | 7 | 7.5
2025-04-14 | 11918 | 58 | 6912.44 | 3.6 | 429.048 | 2001 | 217 | 108.4458 | 4.8 | 22 | 0.61 | 198 | 15.6 | 488 | 45 | 253 | 11 | 7.51
2025-04-15 | 12165 | 58 | 7055.7 | 3.4 | 413.61 | 2008 | 193 | 96.1155 | 5.1 | 23 | 0.44 | 139 | 9.9 | 400 | 27.6 | 251 | 8.6 | 7.47
2025-04-16 | 12168 | 58 | 7057.44 | 3.3 | 401.544 | 1993 | 189 | 94.8319 | 4.95 | 23 | 0.67 | 158 | 9.7 | 349 | 30 | 248 | 8 | 7.4
2025-04-17 | 11694 | 60 | 7016.4 | 3.5 | 409.29 | 2015 | 186 | 92.3077 | 5.2 | 23.5 | 0.34 | 130 | 9.4 | 338 | 27 | 252 | 8 | 7.36
2025-04-18 | 11685 | 60 | 7011 | 3.5 | 408.975 | 2010 | 183 | 91.0448 | 4.8 | 24 | 0.54 | 147 | 9.3 | 337 | 28.6 | 246 | 8.7 | 7.44
2025-04-19 | 11956 | 60 | 7173.6 | 3.5 | 418.46 | 2012 | 182 | 90.4573 | 5.1 | 22 | 0.56 | 160 | 9 | 492 | 32 | 250 | 7.3 | 7.4
2025-04-20 | 11914 | 60 | 7148.4 | 3.4 | 405.076 | 2026 | 201 | 99.2103 | 4.92 | 24 | 0.87 | 138 | 10.6 | 477 | 26.2 | 254 | 8.4 | 7.42
2025-04-21 | 11531 | 60 | 6918.6 | 3.4 | 392.054 | 2017 | 186 | 92.2162 | 5.1 | 20 | 0.82 | 122 | 9.6 | 484 | 32 | 249 | 7 | 7.37
2025-04-22 | 11268 | 60 | 6760.8 | 3.6 | 405.648 | 1990 | 197 | 98.995 | 5 | 22 | 0.44 | 134 | 9.3 | 466 | 30.6 | 251 | 7.3 | 7.45
2025-04-23 | 11293 | 60 | 6775.8 | 3.6 | 406.548 | 2010 | 199 | 99.005 | 5.05 | 22 | 0.59 | 180 | 11 | 481 | 31.1 | 247 | 8 | 7.39
2025-04-24 | 11558 | 60 | 6934.8 | 3.3 | 381.414 | 2018 | 197 | 97.6214 | 3.2 | 21 | 0.38 | 135 | 10 | 480 | 26 | 253 | 8 | 7.4
2025-04-25 | 11418 | 60 | 6850.8 | 3.5 | 399.63 | 2025 | 213 | 105.1852 | 2.9 | 23 | 0.84 | 168 | 13 | 468 | 37.4 | 248 | 11 | 7.37
2025-04-26 | 11298 | 60 | 6778.8 | 3.6 | 406.728 | 1998 | 202 | 101.1011 | 3.42 | 22 | 0.82 | 127 | 12 | 467 | 33.3 | 252 | 9.7 | 7.43
2025-04-27 | 11296 | 60 | 6777.6 | 3.6 | 406.656 | 1995 | 208 | 104.2607 | 3.1 | 24 | 0.46 | 157 | 11 | 470 | 34 | 246 | 8.1 | 7.4
2025-04-28 | 11641 | 60 | 6984.6 | 3.4 | 395.794 | 2015 | 191 | 94.7891 | 2.8 | 23 | 0.67 | 157 | 9 | 492 | 29.3 | 251 | 8 | 7.42
2025-04-29 | 11540 | 60 | 6924 | 3.3 | 380.82 | 2003 | 201 | 100.3495 | 3.5 | 22.6 | 0.65 | 180 | 14 | 487 | 45 | 249 | 11 | 7.36
2025-04-30 | 11557 | 60 | 6934.2 | 3.5 | 404.495 | 2010 | 208 | 103.4826 | 2.9 | 23.6 | 0.37 | 143 | 10.7 | 493 | 31.7 | 254 | 8.5 | 7.44
2025-05-01 | 11182 | 60 | 6709.2 | 3.5 | 391.37 | 1958 | 207 | 105.7201 | 3.3 | 25 | 0.75 | 150 | 10.6 | 483 | 28.7 | 247 | 8.3 | 7.4
2025-05-02 | 11170 | 60 | 6702 | 3.5 | 390.95 | 1952 | 209 | 107.0697 | 3.1 | 25.5 | 0.61 | 165 | 11.8 | 493 | 35 | 250 | 8.2 | 7.42
2025-05-03 | 11644 | 60 | 6986.4 | 3.4 | 395.896 | 1946 | 215 | 110.483 | 3.44 | 26.7 | 0.76 | 144 | 12.2 | 483 | 36.4 | 253 | 10.6 | 7.38
2025-05-04 | 11707 | 60 | 7024.2 | 3.4 | 398.038 | 1945 | 186 | 95.6298 | 2.8 | 26 | 0.6 | 135 | 9.8 | 474 | 35.6 | 245 | 7 | 8
2025-05-05 | 11686 | 60 | 7011.6 | 3.6 | 420.696 | 1970 | 195 | 98.9848 | 3.3 | 26 | 0.27 | 125 | 10 | 467 | 34 | 251 | 8 | 7.94
2025-05-06 | 11557 | 60 | 6934.2 | 3.5 | 404.495 | 1981 | 200 | 100.9591 | 2.95 | 25.8 | 0.47 | 140 | 10.7 | 478 | 34 | 248 | 8.2 | 8.05
2025-05-07 | 11582 | 60 | 6949.2 | 3.5 | 405.37 | 1948 | 208 | 106.7762 | 3.4 | 25 | 0.28 | 155 | 11.4 | 489 | 39 | 252 | 9.3 | 8
2025-05-08 | 11770 | 60 | 7062 | 3.4 | 400.18 | 1974 | 219 | 110.9422 | 3 | 26.5 | 0.86 | 184 | 13 | 400 | 33 | 246 | 9.5 | 8.03
2025-05-09 | 11808 | 60 | 7084.8 | 3.4 | 401.472 | 1979 | 200 | 101.0611 | 1 | 25 | 0.81 | 183 | 10.4 | 308 | 29.7 | 254 | 8.9 | 7.96
2025-05-10 | 11432 | 60 | 6859.2 | 3.6 | 411.552 | 1967 | 217 | 110.3203 | 2.9 | 26.8 | 0.79 | 168 | 12.2 | 466 | 32 | 250 | 9 | 8.06
2025-05-11 | 11449 | 60 | 6869.4 | 3.5 | 400.715 | 1954 | 221 | 113.1013 | 3.2 | 27 | 0.46 | 169 | 13 | 477 | 35.8 | 247 | 9 | 8
2025-05-12 | 11279 | 60 | 6767.4 | 3.6 | 406.044 | 1956 | 203 | 103.7832 | 3.1 | 26 | 0.31 | 162 | 13.4 | 400 | 33 | 253 | 8.3 | 8.02
2025-05-13 | 11349 | 60 | 6809.4 | 3.6 | 408.564 | 1967 | 218 | 110.8287 | 3.42 | 27 | 0.82 | 168 | 16 | 543 | 45 | 270 | 10.4 | 7.97
2025-05-14 | 11546 | 60 | 6927.6 | 3.4 | 392.564 | 1955 | 206 | 105.3708 | 3.5 | 27 | 0.87 | 170 | 12.2 | 453 | 35 | 248 | 9 | 8.04
2025-05-15 | 11770 | 60 | 7062 | 3.3 | 388.41 | 1964 | 211 | 107.4338 | 3.1 | 27.3 | 0.32 | 172 | 11.7 | 322 | 29.3 | 252 | 10 | 8
2025-05-16 | 11645 | 60 | 6987 | 3.5 | 407.575 | 1950 | 192 | 98.4615 | 3.45 | 26.5 | 0.58 | 159 | 10 | 331 | 28 | 189 | 7 | 8.04
2025-05-17 | 11918 | 60 | 7150.8 | 3.5 | 417.13 | 1963 | 200 | 101.8849 | 3 | 25 | 0.31 | 160 | 11.3 | 543 | 35 | 250 | 9 | 7.95
2025-05-18 | 11546 | 60 | 6927.6 | 3.5 | 404.11 | 1979 | 198 | 100.0505 | 2.9 | 25.6 | 0.71 | 144 | 11.3 | 522 | 37 | 254 | 8.5 | 8.05
2025-05-19 | 11561 | 60 | 6936.6 | 3.4 | 393.074 | 1982 | 197 | 99.3946 | 3.42 | 26 | 0.75 | 145 | 11.3 | 488 | 40.9 | 249 | 8 | 8
2025-05-20 | 11432 | 60 | 6859.2 | 3.4 | 388.688 | 1978 | 203 | 102.6289 | 3.1 | 26 | 0.35 | 168 | 11.5 | 500 | 44.6 | 251 | 8 | 8.02
2025-05-21 | 11487 | 60 | 6892.2 | 3.6 | 413.532 | 1971 | 224 | 113.6479 | 1 | 26 | 0.57 | 167 | 10.8 | 422 | 34 | 247 | 8 | 7.6
2025-05-22 | 11332 | 60 | 6799.2 | 3.6 | 407.952 | 1978 | 191 | 96.5622 | 3.5 | 27.4 | 0.62 | 153 | 12.2 | 460 | 32 | 253 | 8 | 7.55
2025-05-23 | 11296 | 60 | 6777.6 | 3.4 | 384.064 | 1948 | 194 | 99.5893 | 2.9 | 26.5 | 0.44 | 168 | 11.7 | 305 | 27 | 248 | 7 | 7.64
2025-05-24 | 11685 | 60 | 7011 | 3.3 | 385.605 | 1970 | 189 | 95.9391 | 3.3 | 26 | 0.82 | 164 | 11.1 | 470 | 34 | 252 | 10.1 | 7.6
2025-05-25 | 11696 | 60 | 7017.6 | 3.5 | 409.36 | 1952 | 209 | 107.0697 | 3.1 | 27 | 0.54 | 164 | 11.5 | 358 | 31 | 246 | 7 | 7.62
2025-05-26 | 11378 | 60 | 6826.8 | 3.4 | 386.852 | 1969 | 193 | 98.0193 | 3.44 | 25 | 0.4 | 144 | 11.6 | 343 | 32.9 | 251 | 9 | 7.57
2025-05-27 | 11168 | 60 | 6700.8 | 3.4 | 379.712 | 1955 | 219 | 112.0205 | 1 | 27.5 | 0.61 | 153 | 15.5 | 480 | 40 | 249 | 11 | 7.65
2025-05-28 | 11171 | 60 | 6702.6 | 3.6 | 402.156 | 1983 | 210 | 105.9002 | 3.3 | 27 | 0.73 | 178 | 11.6 | 478 | 34 | 254 | 8 | 7.6
2025-05-29 | 11416 | 60 | 6849.6 | 3.3 | 376.728 | 1977 | 200 | 101.1634 | 2.95 | 27.4 | 0.4 | 164 | 12.5 | 532 | 40 | 247 | 9 | 7.61
2025-05-30 | 11432 | 60 | 6859.2 | 3.5 | 400.12 | 1970 | 220 | 111.6751 | 3.4 | 28 | 0.47 | 154 | 13.2 | 489 | 38.1 | 250 | 8 | 7.57
2025-05-31 | 11474 | 60 | 6884.4 | 3.6 | 413.064 | 2160 | 221 | 102.3148 | 3 | 27.5 | 0.9 | 183 | 11.6 | 430 | 34 | 253 | 9 | 7.63
2025-06-01 | 11270 | 60 | 6762 | 3.6 | 405.72 | 2142 | 207 | 96.6387 | 3.52 | 27.8 | 0.68 | 173 | 11.8 | 444 | 31 | 245 | 9 | 7.6
2025-06-02 | 11186 | 60 | 6711.6 | 3.3 | 369.138 | 2154 | 197 | 91.4578 | 2.9 | 29 | 0.55 | 193 | 12.7 | 444 | 31 | 251 | 10.8 | 7.62
2025-06-03 | 11307 | 60 | 6784.2 | 3.5 | 395.745 | 2131 | 212 | 99.4838 | 3.2 | 30 | 0.6 | 162 | 14.1 | 477 | 38 | 248 | 10.3 | 7.56
2025-06-04 | 11321 | 60 | 6792.6 | 3.6 | 407.556 | 2132 | 226 | 106.0038 | 3.1 | 32 | 0.35 | 181 | 14.3 | 470 | 39.6 | 252 | 13 | 7.64
2025-06-05 | 11296 | 60 | 6777.6 | 3.6 | 406.656 | 2161 | 232 | 107.3577 | 3.42 | 31.5 | 0.42 | 174 | 14.9 | 500 | 47.3 | 246 | 11 | 7.6
2025-06-06 | 11168 | 60 | 6700.8 | 3.4 | 379.712 | 2135 | 211 | 98.829 | 3.5 | 33 | 0.48 | 162 | 9.5 | 430 | 30.6 | 103 | 7 | 7.61
2025-06-07 | 11171 | 60 | 6702.6 | 3.3 | 368.643 | 2153 | 197 | 91.5002 | 3.1 | 32 | 0.64 | 194 | 10 | 357 | 35 | 250 | 9 | 7.58
2025-06-08 | 11036 | 60 | 6621.6 | 3.5 | 386.26 | 2145 | 216 | 100.6993 | 3.45 | 30 | 0.41 | 191 | 13.3 | 400 | 36 | 247 | 10 | 7.6
2025-06-09 | 11282 | 60 | 6769.2 | 3.5 | 394.87 | 2142 | 210 | 98.0392 | 3.2 | 30.6 | 0.41 | 176 | 14.9 | 388 | 37 | 253 | 10 | 7.56
2025-06-10 | 11284 | 60 | 6770.4 | 3.5 | 394.94 | 2155 | 219 | 101.6241 | 2.9 | 32 | 0.31 | 171 | 15.4 | 396 | 39 | 251 | 9.9 | 7.63
2025-06-11 | 11046 | 60 | 6627.6 | 3.4 | 375.564 | 2146 | 208 | 96.9245 | 3.42 | 31 | 0.67 | 190 | 14.4 | 380 | 37.4 | 248 | 8 | 7.6
2025-06-12 | 11046 | 60 | 6627.6 | 3.4 | 375.564 | 2158 | 207 | 95.9222 | 3.1 | 33 | 0.48 | 191 | 15 | 440 | 44 | 252 | 8.9 | 7.62
2025-06-13 | 11546 | 60 | 6927.6 | 3.6 | 415.656 | 2158 | 199 | 92.215 | 2.8 | 29 | 0.84 | 169 | 13 | 400 | 34 | 246 | 10 | 7.57
2025-06-14 | 11546 | 60 | 6927.6 | 3.3 | 381.018 | 2157 | 213 | 98.7483 | 3.5 | 31 | 0.81 | 182 | 14.2 | 387 | 37 | 250 | 10 | 7.65
2025-06-15 | 11307 | 60 | 6784.2 | 3.5 | 395.745 | 2146 | 208 | 96.9245 | 2.9 | 29 | 0.31 | 187 | 10 | 300 | 28 | 254 | 8 | 7.6
2025-06-16 | 11296 | 60 | 6777.6 | 3.6 | 406.656 | 2168 | 199 | 91.7897 | 3.3 | 33 | 0.43 | 184 | 9.4 | 380 | 33 | 249 | 8 | 7.61
2025-06-17 | 11171 | 60 | 6702.6 | 3.6 | 402.156 | 2134 | 217 | 101.687 | 3.1 | 31 | 0.69 | 174 | 14.5 | 400 | 39 | 251 | 9 | 7.56
2025-06-18 | 10925 | 60 | 6555 | 3.4 | 371.45 | 2147 | 204 | 95.0163 | 3.44 | 28 | 0.4 | 161 | 12 | 420 | 34.6 | 247 | 9 | 7.64
2025-06-19 | 10949 | 60 | 6569.4 | 3.3 | 361.317 | 2168 | 221 | 101.9373 | 2.8 | 30 | 0.35 | 162 | 13.5 | 440 | 38 | 253 | 10.6 | 7.6
2025-06-20 | 10794 | 60 | 6476.4 | 3.5 | 377.79 | 2139 | 206 | 96.3067 | 3.3 | 32 | 0.86 | 183.2 | 13 | 480 | 35 | 248 | 8 | 7.62
2025-06-21 | 10807 | 60 | 6484.2 | 3.5 | 378.245 | 2156 | 207 | 96.0111 | 2.95 | 30 | 0.63 | 173 | 14.4 | 430 | 41.6 | 252 | 11 | 7.57
2025-06-22 | 10987 | 60 | 6592.2 | 3.5 | 384.545 | 2162 | 213 | 98.5199 | 3.4 | 33 | 0.57 | 170 | 15.1 | 430 | 39.8 | 246 | 10.1 | 7.64
2025-06-23 | 10998 | 60 | 6598.8 | 3.4 | 373.932 | 2160 | 218 | 100.9259 | 3 | 30 | 0.76 | 188 | 14.4 | 390 | 36 | 251 | 10.3 | 7.6
2025-06-24 | 11296 | 60 | 6777.6 | 3.4 | 384.064 | 2160 | 194 | 89.8148 | 3.52 | 31.7 | 0.78 | 165 | 7.6 | 300 | 21.8 | 140 | 6 | 7.61
2025-06-25 | 10916 | 60 | 6549.6 | 3.6 | 392.976 | 2132 | 222 | 104.1276 | 2.9 | 33 | 0.39 | 175 | 13.5 | 330 | 33 | 254 | 9 | 7.58
2025-06-26 | 11307 | 60 | 6784.2 | 3.6 | 407.052 | 2148 | 229 | 106.6108 | 3.2 | 32 | 0.33 | 166 | 14 | 420 | 45 | 247 | 10.6 | 7.5
2025-06-27 | 11421 | 60 | 6852.6 | 3.4 | 388.314 | 2134 | 220 | 103.0928 | 3.1 | 29.5 | 0.54 | 176 | 13 | 380 | 37.8 | 250 | 9.4 | 7.45
2025-06-28 | 11449 | 60 | 6869.4 | 3.6 | 412.164 | 2161 | 203 | 93.938 | 3.42 | 31 | 0.54 | 192 | 9.5 | 320 | 29.8 | 253 | 6.6 | 7.54
2025-06-29 | 11307 | 60 | 6784.2 | 3.6 | 407.052 | 2170 | 198 | 91.2442 | 3.5 | 30.6 | 0.56 | 170 | 13.3 | 450 | 38.8 | 245 | 10 | 7.5
2025-06-30 | 11057 | 60 | 6634.2 | 3.4 | 375.938 | 2103 | 222 | 105.5635 | 3.1 | 32 | 0.73 | 180 | 15.5 | 370 | 36 | 251 | 13.4 | 7.52
2025-07-01 | 11046 | 60 | 6627.6 | 3.3 | 364.518 | 2067 | 217 | 104.9831 | 3.45 | 32 | 0.69 | 197 | 14.1 | 378 | 40.2 | 248 | 9.9 | 7.47
2025-07-02 | 10796 | 60 | 6477.6 | 3.5 | 377.86 | 2099 | 229 | 109.0996 | 5.1 | 33 | 0.89 | 170 | 16 | 370 | 38 | 252 | 10 | 7.55
2025-07-03 | 11046 | 60 | 6627.6 | 3.5 | 386.61 | 2081 | 199 | 95.6271 | 4.7 | 31.8 | 0.33 | 164 | 9.4 | 354 | 34 | 246 | 8.3 | 7.5
2025-07-04 | 11060 | 60 | 6636 | 3.5 | 387.1 | 2102 | 206 | 98.0019 | 5.24 | 34 | 0.52 | 189 | 9.8 | 270 | 32 | 254 | 7.4 | 7.52
2025-07-05 | 10921 | 60 | 6552.6 | 3.4 | 371.314 | 2073 | 222 | 107.0912 | 4.9 | 32 | 0.48 | 176 | 14.4 | 470 | 45.5 | 250 | 14 | 7.47
2025-07-06 | 10932 | 60 | 6559.2 | 3.4 | 371.688 | 2090 | 213 | 101.9139 | 4.8 | 32 | 0.81 | 170 | 15.5 | 490 | 37 | 247 | 11 | 7.53
2025-07-07 | 10657 | 60 | 6394.2 | 3.5 | 372.995 | 2085 | 226 | 108.3933 | 5.3 | 32 | 0.43 | 197 | 15.6 | 380 | 38 | 253 | 12 | 7.5
2025-07-08 | 10671 | 60 | 6402.6 | 3.5 | 373.485 | 2098 | 232 | 110.5815 | 4.95 | 29.6 | 0.39 | 194 | 13.9 | 360 | 34.1 | 251 | 10.7 | 7.52
2025-07-09 | 11057 | 60 | 6634.2 | 3.6 | 398.052 | 2078 | 222 | 106.8335 | 5.2 | 33 | 0.55 | 182 | 15.5 | 460 | 44 | 248 | 11.3 | 7.46
2025-07-10 | 11074 | 60 | 6644.4 | 3.5 | 387.59 | 2094 | 211 | 100.7641 | 5 | 33 | 0.54 | 187 | 15.2 | 480 | 48 | 252 | 11.1 | 7.54
2025-07-11 | 10794 | 60 | 6476.4 | 3.5 | 377.79 | 2076 | 213 | 102.6012 | 5.14 | 32 | 0.45 | 170 | 14.6 | 330 | 40 | 246 | 11 | 7.5
2025-07-12 | 10797 | 60 | 6478.2 | 3.5 | 377.895 | 2071 | 221 | 106.7117 | 4.8 | 32 | 0.49 | 190 | 14.4 | 422 | 39 | 250 | 11.1 | 7.51
2025-07-13 | 10599 | 60 | 6359.4 | 3.4 | 360.366 | 2072 | 209 | 100.8687 | 5.2 | 33.7 | 0.85 | 195 | 16.1 | 540 | 44 | 254 | 13 | 7
2025-07-14 | 10546 | 60 | 6327.6 | 3.6 | 379.656 | 2080 | 232 | 111.5385 | 4.95 | 33 | 0.55 | 164 | 15.3 | 255 | 38 | 249 | 11.6 | 7.9
2025-07-15 | 10682 | 60 | 6409.2 | 3.3 | 352.506 | 2102 | 216 | 102.7593 | 5.3 | 32 | 0.81 | 168 | 14.4 | 360 | 36.8 | 251 | 9.6 | 7
2025-07-16 | 10641 | 60 | 6384.6 | 3.5 | 372.435 | 2084 | 238 | 114.2035 | 4.8 | 32 | 0.62 | 174 | 15 | 341 | 43.5 | 247 | 10.3 | 7.94
2025-07-17 | 10671 | 60 | 6402.6 | 3.6 | 384.156 | 2104 | 198 | 94.1065 | 5.2 | 31 | 0.3 | 168 | 9 | 344 | 28 | 253 | 8 | 7.9
2025-07-18 | 10922 | 60 | 6553.2 | 3.6 | 393.192 | 2097 | 237 | 113.0186 | 4.92 | 31.5 | 0.9 | 192 | 14.3 | 362 | 39.8 | 248 | 9.2 | 7.92
2025-07-19 | 10932 | 60 | 6559.2 | 3.4 | 371.688 | 2066 | 200 | 96.8054 | 5.1 | 32 | 0.8 | 183 | 10 | 360 | 31 | 252 | 7.1 | 7.87
2025-07-20 | 10666 | 60 | 6399.6 | 3.3 | 351.978 | 2076 | 214 | 103.0829 | 4.9 | 34 | 0.88 | 190 | 15.7 | 362 | 44 | 246 | 9 | 7.95
2025-07-21 | 10666 | 60 | 6399.6 | 3.5 | 373.31 | 2093 | 210 | 100.3344 | 5.05 | 32 | 0.85 | 185 | 14 | 350 | 44 | 251 | 9.1 | 7.9
2025-07-22 | 10682 | 60 | 6409.2 | 3.5 | 373.87 | 2101 | 226 | 107.5678 | 4.8 | 33 | 0.8 | 200 | 15 | 366 | 42 | 249 | 11 | 7.91
2025-07-23 | 10932 | 60 | 6559.2 | 3.5 | 382.62 | 2068 | 227 | 109.7679 | 4.5 | 32 | 0.37 | 180 | 16 | 350 | 45 | 254 | 10.1 | 7.87
2025-07-24 | 10987 | 60 | 6592.2 | 3.4 | 373.558 | 2081 | 215 | 103.3157 | 4.94 | 34 | 0.58 | 200 | 15.5 | 361 | 35 | 247 | 11 | 7.93
2025-07-25 | 10670 | 60 | 6402 | 3.4 | 362.78 | 2090 | 208 | 99.5215 | 4.7 | 29 | 0.51 | 169 | 12.9 | 364 | 36.8 | 250 | 9.5 | 7.9
2025-07-26 | 10682 | 60 | 6409.2 | 3.6 | 384.552 | 2093 | 219 | 104.6345 | 4.6 | 31 | 0.52 | 165 | 14.6 | 352 | 37.4 | 253 | 10.9 | 7.92
2025-07-27 | 10670 | 60 | 6402 | 3.3 | 352.11 | 2075 | 211 | 101.6867 | 5.1 | 32 | 0.31 | 171 | 14 | 365 | 35 | 245 | 8.8 | 7.86
2025-07-28 | 10682 | 60 | 6409.2 | 3.5 | 373.87 | 2080 | 218 | 104.8077 | 4.75 | 32 | 0.55 | 192 | 15 | 360 | 38 | 251 | 9 | 7.94
2025-07-29 | 10666 | 60 | 6399.6 | 3.6 | 383.976 | 2079 | 233 | 112.0731 | 5 | 32 | 0.89 | 172 | 14.4 | 342 | 39 | 248 | 9.6 | 7.9
2025-07-30 | 10682 | 60 | 6409.2 | 3.6 | 384.552 | 2227 | 230 | 103.278 | 4.8 | 33 | 0.44 | 185 | 15.7 | 460 | 45.9 | 252 | 11 | 7.91
2025-07-31 | 10670 | 65 | 6935.5 | 3.4 | 362.78 | 2252 | 235 | 104.3517 | 4.94 | 34 | 0.76 | 183 | 16.5 | 340 | 39.4 | 246 | 9 | 7.88
2025-08-01 | 10168 | 65 | 6609.2 | 3.3 | 335.544 | 2255 | 209 | 92.6829 | 4.6 | 32 | 0.56 | 197 | 9 | 419 | 29 | 254 | 8 | 7.9
2025-08-02 | 10682 | 65 | 6943.3 | 3.5 | 373.87 | 2229 | 232 | 104.0825 | 5 | 31 | 0.54 | 180 | 14.1 | 428 | 38 | 250 | 9 | 7.84
2025-08-03 | 10670 | 65 | 6935.5 | 3.5 | 373.45 | 2232 | 241 | 107.9749 | 4.75 | 30 | 0.87 | 192 | 14.4 | 420 | 39 | 247 | 8 | 7.93
2025-08-04 | 10682 | 65 | 6943.3 | 3.5 | 373.87 | 2245 | 218 | 97.1047 | 5.1 | 33 | 0.9 | 169 | 10 | 415 | 35 | 253 | 7 | 7.9
2025-08-05 | 10707 | 65 | 6959.55 | 3.4 | 364.038 | 2249 | 223 | 99.1552 | 4.6 | 32 | 0.62 | 165 | 14.9 | 434 | 43 | 251 | 10 | 7.92
2025-08-06 | 10682 | 65 | 6943.3 | 3.4 | 363.188 | 2236 | 224 | 100.1789 | 5 | 30 | 0.72 | 174 | 11.3 | 431 | 38.6 | 248 | 7.6 | 7.86
2025-08-07 | 10668 | 65 | 6934.2 | 3.5 | 373.38 | 2221 | 235 | 105.8082 | 4.72 | 31 | 0.37 | 174 | 13.9 | 430 | 38 | 252 | 10 | 7.95
2025-08-08 | 10168 | 65 | 6609.2 | 3.4 | 345.712 | 2222 | 215 | 96.7597 | 4.9 | 31.7 | 0.46 | 184 | 10 | 408 | 28.7 | 154 | 6 | 7.9
2025-08-09 | 11432 | 65 | 7430.8 | 3.4 | 388.688 | 2221 | 238 | 107.1589 | 4.7 | 32 | 0.88 | 187 | 14.2 | 406 | 38.8 | 250 | 10 | 7.89
2025-08-10 | 11545 | 65 | 7504.25 | 3.6 | 415.62 | 2244 | 237 | 105.615 | 4.85 | 34 | 0.63 | 176 | 13 | 408 | 38.1 | 254 | 10 | 7.91
2025-08-11 | 11557 | 65 | 7512.05 | 3.3 | 381.381 | 2216 | 210 | 94.7653 | 3.4 | 32 | 0.61 | 176 | 10.2 | 432 | 32 | 249 | 7.8 | 7.88
2025-08-12 | 11670 | 65 | 7585.5 | 3.5 | 408.45 | 2225 | 243 | 109.2135 | 3 | 32 | 0.74 | 167 | 14.4 | 428 | 36 | 251 | 9.8 | 7.93
2025-08-13 | 11693 | 65 | 7600.45 | 3.6 | 420.948 | 2219 | 218 | 98.2425 | 3.52 | 32 | 0.31 | 188 | 15 | 407 | 42 | 247 | 10.4 | 7.9
2025-08-14 | 11391 | 65 | 7404.15 | 3.6 | 410.076 | 2249 | 220 | 97.8213 | 3.2 | 29.6 | 0.64 | 186 | 13.7 | 422 | 39.4 | 253 | 10 | 7.92
2025-08-15 | 11766 | 65 | 7647.9 | 3.4 | 400.044 | 2239 | 240 | 107.1907 | 2.9 | 31 | 0.59 | 164 | 14.9 | 407 | 50 | 248 | 11 | 7.86
2025-08-16 | 11932 | 65 | 7755.8 | 3.3 | 393.756 | 2239 | 239 | 106.7441 | 3.6 | 33 | 0.81 | 168 | 15.2 | 420 | 48 | 252 | 9 | 7.94
2025-08-17 | 11920 | 65 | 7748 | 3.5 | 417.2 | 2248 | 245 | 108.9858 | 3.1 | 30 | 0.37 | 170 | 13.5 | 428 | 35 | 246 | 10 | 7.9
2025-08-18 | 11932 | 65 | 7755.8 | 3.5 | 417.62 | 2238 | 206 | 92.0465 | 3.4 | 32 | 0.88 | 163 | 13 | 300 | 24 | 251 | 11 | 7.91
2025-08-19 | 12945 | 65 | 8414.25 | 3.5 | 453.075 | 2247 | 211 | 93.903 | 3.2 | 30 | 0.32 | 185 | 14.4 | 300 | 35 | 249 | 9 | 7.87
2025-08-20 | 12668 | 65 | 8234.2 | 3.4 | 430.712 | 2231 | 210 | 94.1282 | 3.54 | 29 | 0.39 | 194 | 13.4 | 400 | 36 | 254 | 8.5 | 7.8
2025-08-21 | 12732 | 65 | 8275.8 | 3.4 | 432.888 | 2224 | 217 | 97.5719 | 2.9 | 30 | 0.64 | 169 | 14.5 | 340 | 41 | 247 | 8.9 | 7.75
2025-08-22 | 12936 | 65 | 8408.4 | 3.6 | 465.696 | 2238 | 225 | 100.5362 | 3.4 | 33 | 0.7 | 173 | 14 | 455 | 40 | 250 | 13 | 7.84
2025-08-23 | 12957 | 65 | 8422.05 | 3.6 | 466.452 | 2215 | 222 | 100.2257 | 3.15 | 30 | 0.42 | 196 | 13.2 | 370 | 35 | 253 | 9 | 7.8
2025-08-24 | 13045 | 65 | 8479.25 | 3.4 | 443.53 | 2238 | 236 | 105.4513 | 3.6 | 29.8 | 0.35 | 191.4 | 13.7 | 370 | 36.2 | 245 | 9 | 7.82
2025-08-25 | 12957 | 65 | 8422.05 | 3.3 | 427.581 | 2223 | 244 | 109.7616 | 2.9 | 31 | 0.83 | 187 | 13.7 | 300 | 31 | 251 | 10.7 | 7.77
2025-08-26 | 12945 | 60 | 7767 | 3.5 | 453.075 | 2245 | 207 | 92.2049 | 3.4 | 30.6 | 0.43 | 162 | 8.7 | 380 | 28 | 248 | 6 | 7.85
2025-08-27 | 12807 | 60 | 7684.2 | 3.5 | 448.245 | 2231 | 223 | 99.9552 | 3.12 | 32 | 0.64 | 200 | 9.6 | 530 | 26.6 | 252 | 8 | 7.8
2025-08-28 | 12907 | 60 | 7744.2 | 3.5 | 451.745 | 2219 | 231 | 104.1009 | 3.3 | 31 | 0.66 | 166 | 14.9 | 440 | 40 | 246 | 13 | 7.81
2025-08-29 | 12907 | 60 | 7744.2 | 3.4 | 438.838 | 2300 | 237 | 103.0435 | 3.1 | 30 | 0.53 | 171 | 14.2 | 326 | 36.5 | 254 | 9 | 7.76
2025-08-30 | 12682 | 60 | 7609.2 | 3.4 | 431.188 | 2284 | 243 | 106.3923 | 3.25 | 30 | 0.64 | 192 | 15.6 | 430 | 42.1 | 250 | 10 | 7.83
2025-08-31 | 13041 | 60 | 7824.6 | 3.6 | 469.476 | 2308 | 248 | 107.4523 | 3.1 | 29 | 0.6 | 189 | 14 | 266 | 33 | 247 | 10.2 | 7.8
2025-09-01 | 12693 | 60 | 7615.8 | 3.3 | 418.869 | 2294 | 219 | 95.4664 | 2.8 | 29 | 0.86 | 158 | 12 | 320 | 29.9 | 253 | 9 | 7.82
2025-09-02 | 12682 | 60 | 7609.2 | 3.5 | 443.87 | 2301 | 220 | 95.6106 | 3.32 | 30 | 0.63 | 183 | 12 | 300 | 42.8 | 251 | 9.5 | 7.76
2025-09-03 | 12957 | 60 | 7774.2 | 3.6 | 466.452 | 2295 | 236 | 102.8322 | 3 | 28.5 | 0.72 | 157 | 12.7 | 470 | 32 | 248 | 9.3 | 7.84
2025-09-04 | 13045 | 60 | 7827 | 3.6 | 469.62 | 2308 | 218 | 94.4541 | 2.7 | 30 | 0.42 | 160 | 10 | 440 | 27 | 252 | 8.7 | 7.8
2025-09-05 | 12957 | 60 | 7774.2 | 3.4 | 440.538 | 2274 | 242 | 106.4204 | 3.4 | 28 | 0.52 | 168 | 12.2 | 400 | 40 | 246 | 9 | 7.81
2025-09-06 | 12907 | 60 | 7744.2 | 3.3 | 425.931 | 2285 | 226 | 98.9059 | 2.9 | 30 | 0.69 | 163 | 13.1 | 430 | 25 | 250 | 8.9 | 8
2025-09-07 | 12932 | 60 | 7759.2 | 3.5 | 452.62 | 2300 | 234 | 101.7391 | 3.2 | 26 | 0.46 | 181 | 11.2 | 330 | 29.4 | 254 | 9.5 | 7.6
2025-09-08 | 12945 | 60 | 7767 | 3.5 | 453.075 | 2291 | 221 | 96.4644 | 3 | 30 | 0.47 | 154 | 14.4 | 330 | 39 | 249 | 10.6 | 7.54
2025-09-09 | 12807 | 60 | 7684.2 | 3.5 | 448.245 | 2279 | 253 | 111.0136 | 3.34 | 27 | 0.74 | 161 | 12.2 | 370 | 36.8 | 251 | 9.1 | 7.63
2025-09-10 | 12907 | 60 | 7744.2 | 3.4 | 438.838 | 2299 | 214 | 93.0839 | 2.7 | 29 | 0.32 | 168 | 13.9 | 370 | 37 | 247 | 8.3 | 7.6
2025-09-11 | 12907 | 60 | 7744.2 | 3.4 | 438.838 | 2293 | 220 | 95.9442 | 3.2 | 29 | 0.56 | 170 | 13.2 | 330 | 34 | 253 | 8 | 7.62
2025-09-12 | 12907 | 60 | 7744.2 | 3.3 | 425.931 | 2281 | 251 | 110.0395 | 2.95 | 31 | 0.91 | 153 | 15 | 340 | 40.3 | 248 | 10 | 7.57
2025-09-13 | 12706 | 60 | 7623.6 | 3.5 | 444.71 | 2278 | 226 | 99.2098 | 3.4 | 28 | 0.9 | 180 | 13.1 | 370 | 40.2 | 252 | 9 | 7.64
2025-09-14 | 12906 | 60 | 7743.6 | 3.5 | 451.71 | 2286 | 230 | 100.6124 | 2.7 | 27 | 0.32 | 148 | 12.6 | 390 | 38 | 246 | 10 | 7.6
2025-09-15 | 12906 | 60 | 7743.6 | 3.5 | 451.71 | 2302 | 228 | 99.0443 | 3.2 | 29 | 0.4 | 169 | 12.4 | 330 | 35 | 100 | 7 | 7.61
2025-09-16 | 12907 | 60 | 7744.2 | 3.4 | 438.838 | 2301 | 240 | 104.3025 | 2.92 | 29 | 0.44 | 174 | 13.5 | 340 | 38 | 249 | 10 | 7.57
2025-09-17 | 12794 | 67 | 8571.98 | 3.6 | 460.584 | 2304 | 246 | 106.7708 | 3.1 | 27 | 0.86 | 171 | 11.5 | 400 | 29.3 | 254 | 9 | 7.63
2025-09-18 | 12807 | 67 | 8580.69 | 3.3 | 422.631 | 2288 | 222 | 97.028 | 2.9 | 30 | 0.86 | 166 | 13.5 | 430 | 37 | 247 | 10.6 | 7.6
2025-09-19 | 13170 | 67 | 8823.9 | 3.5 | 460.95 | 2281 | 247 | 108.2858 | 3.05 | 30 | 0.82 | 164 | 14.4 | 420 | 39 | 250 | 11 | 7.62
2025-09-20 | 13457 | 67 | 9016.19 | 3.6 | 484.452 | 2309 | 252 | 109.1382 | 3.3 | 30 | 0.5 | 179 | 13 | 380 | 38 | 253 | 10 | 7.56
2025-09-21 | 13432 | 67 | 8999.44 | 3.6 | 483.552 | 2275 | 218 | 95.8242 | 2.9 | 29 | 0.37 | 169 | 12.8 | 326 | 34.8 | 245 | 10 | 7.64
2025-09-22 | 12907 | 67 | 8647.69 | 3.4 | 438.838 | 2279 | 238 | 104.4318 | 3.52 | 27 | 0.8 | 166 | 12.9 | 324 | 38.7 | 251 | 9 | 7.6
2025-09-23 | 12957 | 67 | 8681.19 | 3.3 | 427.581 | 2283 | 216 | 94.6124 | 3.1 | 30 | 0.71 | 147 | 13.7 | 444 | 42.2 | 248 | 10.8 | 7.61
2025-09-24 | 13045 | 67 | 8740.15 | 3.5 | 456.575 | 2293 | 240 | 104.6664 | 2.8 | 26 | 0.66 | 155 | 10.9 | 318 | 33.5 | 252 | 8 | 7.58
2025-09-25 | 12957 | 67 | 8681.19 | 3.5 | 453.495 | 2304 | 214 | 92.8819 | 3.6 | 30 | 0.89 | 155 | 13 | 344 | 38.4 | 246 | 8.7 | 7.6
2025-09-26 | 12907 | 67 | 8647.69 | 3.6 | 464.652 | 2274 | 231 | 101.5831 | 3 | 29 | 0.68 | 158 | 12.8 | 322 | 37 | 254 | 10 | 7.55
2025-09-27 | 12682 | 67 | 8496.94 | 3.3 | 418.506 | 2295 | 230 | 100.2179 | 3.4 | 29 | 0.27 | 160 | 13.6 | 325 | 38 | 250 | 9.3 | 7.64
2025-09-28 | 12907 | 67 | 8647.69 | 3.5 | 451.745 | 2380 | 244 | 102.521 | 3.2 | 28 | 0.78 | 155 | 12 | 341 | 32.6 | 247 | 10 | 7.6
2025-09-29 | 12907 | 67 | 8647.69 | 3.6 | 464.652 | 2365 | 252 | 106.5539 | 3.54 | 30 | 0.37 | 150 | 14 | 328 | 40.3 | 253 | 10 | 7.62
2025-09-30 | 12907 | 67 | 8647.69 | 3.6 | 464.652 | 2359 | 221 | 93.6838 | 2.8 | 30 | 0.69 | 177 | 13.6 | 319 | 38 | 251 | 9.9 | 7.57
2025-10-01 | 12670 | 67 | 8488.9 | 3.4 | 430.78 | 2346 | 230 | 98.0392 | 3.4 | 26 | 0.86 | 147 | 8 | 326 | 34.7 | 248 | 7.2 | 7.65
2025-10-02 | 12707 | 67 | 8513.69 | 3.3 | 419.331 | 2374 | 253 | 106.5712 | 3.15 | 26 | 0.35 | 178 | 12 | 500 | 41 | 252 | 9 | 7.6
2025-10-03 | 12936 | 67 | 8667.12 | 3.5 | 452.76 | 2371 | 227 | 95.7402 | 3.6 | 25 | 0.34 | 171 | 10.7 | 328 | 34 | 246 | 8.2 | 7.61
2025-10-04 | 12957 | 67 | 8681.19 | 3.5 | 453.495 | 2345 | 242 | 103.1983 | 2.8 | 24.9 | 0.34 | 153 | 10.5 | 329 | 29 | 250 | 8 | 7.56
2025-10-05 | 13045 | 59 | 7696.55 | 3.5 | 456.575 | 2365 | 226 | 95.5603 | 3.4 | 25.3 | 0.62 | 146 | 11.1 | 336 | 29.4 | 254 | 8 | 7.63
2025-10-06 | 12957 | 59 | 7644.63 | 3.4 | 440.538 | 2373 | 246 | 103.6662 | 3.12 | 25 | 0.44 | 152 | 10 | 317 | 35 | 249 | 6.8 | 7.6
2025-10-07 | 12907 | 59 | 7615.13 | 3.4 | 438.838 | 2361 | 241 | 102.0754 | 3.3 | 24 | 0.65 | 153 | 10.7 | 331 | 33.5 | 251 | 9 | 7.62
2025-10-08 | 12682 | 59 | 7482.38 | 3.6 | 456.552 | 2348 | 236 | 100.5111 | 3.1 | 22.5 | 0.72 | 168 | 8.9 | 425 | 30.7 | 120 | 7 | 7.57
2025-10-09 | 12906 | 59 | 7614.54 | 3.3 | 425.898 | 2377 | 249 | 104.7539 | 3.25 | 25 | 0.4 | 144 | 12 | 350 | 28.9 | 253 | 9.9 | 7.64
2025-10-10 | 12693 | 59 | 7488.87 | 3.5 | 444.255 | 2368 | 258 | 108.9527 | 3.2 | 22 | 0.67 | 165 | 14 | 470 | 43 | 248 | 11 | 7.6
2025-10-11 | 13207 | 59 | 7792.13 | 3.6 | 475.452 | 2349 | 230 | 97.914 | 2.8 | 24 | 0.44 | 161 | 12 | 430 | 37 | 252 | 9 | 7.61
2025-10-12 | 12795 | 59 | 7549.05 | 3.6 | 460.62 | 2356 | 237 | 100.5942 | 3.42 | 23 | 0.58 | 183 | 10 | 450 | 27.2 | 246 | 6.8 | 7.58
2025-10-13 | 12807 | 59 | 7556.13 | 3.4 | 435.438 | 2375 | 251 | 105.6842 | 3.1 | 24.7 | 0.84 | 176 | 16 | 500 | 41.5 | 251 | 10.3 | 7.5
2025-10-14 | 12795 | 59 | 7549.05 | 3.3 | 422.235 | 2358 | 235 | 99.6607 | 2.7 | 26 | 0.8 | 151 | 11 | 370 | 34 | 249 | 9.2 | 7.44
2025-10-15 | 12807 | 59 | 7556.13 | 3.5 | 448.245 | 2362 | 258 | 109.2295 | 3.5 | 26 | 0.33 | 173 | 10.9 | 380 | 33 | 206 | 9 | 7.53
2025-10-16 | 12794 | 59 | 7548.46 | 3.5 | 447.79 | 2384 | 254 | 106.5436 | 2.9 | 22 | 0.54 | 168 | 10 | 480 | 30 | 247 | 9.1 | 7.5
2025-10-17 | 12818 | 59 | 7562.62 | 3.5 | 448.63 | 2353 | 238 | 101.1475 | 3.3 | 22 | 0.44 | 164 | 11 | 460 | 33 | 250 | 8 | 7.52
2025-10-18 | 12807 | 59 | 7556.13 | 3.4 | 435.438 | 2371 | 247 | 104.1755 | 3.1 | 24 | 0.27 | 184 | 13 | 400 | 36.3 | 253 | 8 | 7.47
2025-10-19 | 13170 | 59 | 7770.3 | 3.4 | 447.78 | 2358 | 222 | 94.1476 | 3.44 | 25 | 0.76 | 142 | 10.4 | 432 | 33 | 245 | 9.8 | 7.54
2025-10-20 | 13457 | 59 | 7939.63 | 3.3 | 444.081 | 2379 | 245 | 102.9844 | 2.8 | 26 | 0.67 | 174 | 13 | 380 | 38 | 251 | 10.6 | 7.5
2025-10-21 | 11420 | 59 | 6737.8 | 3.5 | 399.7 | 2351 | 233 | 99.1068 | 3.3 | 27 | 0.63 | 183 | 12.3 | 390 | 27 | 248 | 9.4 | 7.51
2025-10-22 | 11432 | 59 | 6744.88 | 3.5 | 400.12 | 2361 | 226 | 95.7222 | 2.95 | 22 | 0.74 | 146 | 10.1 | 400 | 30.5 | 200 | 8 | 7.47
2025-10-23 | 11545 | 59 | 6811.55 | 3.5 | 404.075 | 2363 | 227 | 96.0643 | 3.4 | 22 | 0.62 | 168 | 10 | 450 | 32 | 246 | 8 | 7.53
2025-10-24 | 11557 | 57 | 6587.49 | 3.4 | 392.938 | 2385 | 250 | 104.8218 | 3 | 26 | 0.54 | 181 | 11.9 | 530 | 36 | 254 | 8 | 7.5
2025-10-25 | 11670 | 57 | 6651.9 | 3.5 | 408.45 | 2374 | 253 | 106.5712 | 3.52 | 22 | 0.28 | 143 | 13.5 | 540 | 37 | 250 | 10.3 | 7.52
2025-10-26 | 11693 | 57 | 6665.01 | 3.3 | 385.869 | 2361 | 251 | 106.3109 | 2.9 | 26 | 0.32 | 156 | 13 | 480 | 31 | 247 | 9.3 | 7.46
2025-10-27 | 11391 | 57 | 6492.87 | 3.5 | 398.685 | 2357 | 229 | 97.1574 | 3.2 | 25 | 0.83 | 169 | 11 | 500 | 34 | 120 | 7 | 7.54
2025-10-28 | 11766 | 57 | 6706.62 | 3.6 | 423.576 | 2409 | 251 | 104.1926 | 3.1 | 22.5 | 0.84 | 166 | 13 | 400 | 43 | 251 | 10 | 7.5
2025-10-29 | 11807 | 57 | 6729.99 | 3.6 | 425.052 | 2441 | 261 | 106.9234 | 3.42 | 24 | 0.61 | 150 | 15 | 480 | 36 | 248 | 11 | 7.51
2025-10-30 | 10670 | 57 | 6081.9 | 3.4 | 362.78 | 2414 | 238 | 98.5915 | 3.5 | 25 | 0.8 | 178 | 10 | 490 | 34.3 | 252 | 8 | 7.47
2025-10-31 | 10670 | 57 | 6081.9 | 3.3 | 352.11 | 2425 | 262 | 108.0412 | 3.1 | 25 | 0.64 | 168 | 14 | 480 | 38 | 246 | 9.7 | 7.8
2025-11-01 | 10685 | 57 | 6090.45 | 3.5 | 373.975 | 2414 | 253 | 104.8053 | 3.45 | 18 | 0.36 | 144 | 13 | 542 | 37 | 250 | 11 | 7.74
2025-11-02 | 10920 | 57 | 6224.4 | 3.5 | 382.2 | 2436 | 241 | 98.9327 | 3.6 | 22 | 0.35 | 135 | 9.2 | 480 | 26 | 190 | 7 | 7.83
2025-11-03 | 10707 | 57 | 6102.99 | 3.5 | 374.745 | 2409 | 249 | 103.3624 | 3.2 | 23 | 0.46 | 133 | 10 | 500 | 30 | 249 | 8 | 7.8
2025-11-04 | 10670 | 57 | 6081.9 | 3.4 | 362.78 | 2417 | 229 | 94.7456 | 3.82 | 18 | 0.84 | 143 | 9.5 | 470 | 35 | 251 | 9 | 7.82
2025-11-05 | 10168 | 57 | 5795.76 | 3.4 | 345.712 | 2433 | 253 | 103.9868 | 3.4 | 18 | 0.77 | 146 | 13.4 | 540 | 40 | 247 | 9.2 | 7.77
2025-11-06 | 10682 | 57 | 6088.74 | 3.6 | 384.552 | 2416 | 256 | 105.9603 | 3.1 | 18 | 0.81 | 185 | 15 | 500 | 47 | 253 | 11 | 7.84
2025-11-07 | 10670 | 57 | 6081.9 | 3.5 | 373.45 | 2421 | 237 | 97.8934 | 3.9 | 21 | 0.84 | 141 | 8.5 | 500 | 32.4 | 248 | 7.4 | 7.8
2025-11-08 | 10669 | 57 | 6081.33 | 3.5 | 373.415 | 2422 | 232 | 95.7886 | 3.3 | 22 | 0.4 | 139 | 9 | 322 | 31 | 130 | 7 | 7.81
2025-11-09 | 10672 | 57 | 6083.04 | 3.4 | 362.848 | 2412 | 249 | 103.2338 | 3.6 | 23 | 0.43 | 146 | 12 | 579 | 41.4 | 246 | 9 | 7.77
2025-11-10 | 11142 | 57 | 6350.94 | 3.4 | 378.828 | 2415 | 245 | 101.4493 | 3.4 | 23 | 0.33 | 138 | 10.4 | 470 | 33.6 | 251 | 7 | 7.83
2025-11-11 | 10168 | 57 | 5795.76 | 3.6 | 366.048 | 2441 | 259 | 106.1041 | 3.84 | 19 | 0.76 | 185 | 16 | 440 | 44 | 249 | 11 | 7.8
2025-11-12 | 10682 | 60 | 6409.2 | 3.3 | 352.506 | 2434 | 254 | 104.355 | 3.1 | 20 | 0.83 | 177 | 15 | 400 | 40 | 254 | 10 | 7.82
2025-11-13 | 10641 | 60 | 6384.6 | 3.5 | 372.435 | 2442 | 251 | 102.7846 | 3.7 | 21 | 0.53 | 139 | 8.5 | 389 | 28 | 247 | 6.6 | 7.76
2025-11-14 | 10532 | 60 | 6319.2 | 3.6 | 379.152 | 2435 | 245 | 100.616 | 3.45 | 23 | 0.66 | 134 | 8.6 | 370 | 25.9 | 250 | 7 | 7.84
2025-11-15 | 10407 | 60 | 6244.2 | 3.6 | 374.652 | 2407 | 256 | 106.3565 | 3.9 | 22 | 0.37 | 157 | 9.5 | 382 | 34 | 253 | 8 | 7.8
2025-11-16 | 10670 | 60 | 6402 | 3.4 | 362.78 | 2437 | 268 | 109.9713 | 3.1 | 18 | 0.86 | 175 | 15 | 400 | 37 | 245 | 12.2 | 7.81
2025-11-17 | 10182 | 60 | 6109.2 | 3.3 | 336.006 | 2429 | 236 | 97.1593 | 3.7 | 20 | 0.81 | 127 | 7.8 | 396 | 29.6 | 251 | 6.6 | 7.77
2025-11-18 | 10268 | 60 | 6160.8 | 3.5 | 359.38 | 2437 | 238 | 97.6611 | 3.42 | 20 | 0.89 | 154 | 8 | 399 | 26 | 248 | 7.4 | 7.9
2025-11-19 | 10157 | 60 | 6094.2 | 3.5 | 355.495 | 2445 | 230 | 94.0695 | 3.6 | 21 | 0.78 | 151 | 8.4 | 390 | 32.2 | 252 | 7.8 | 7.85
2025-11-20 | 10170 | 60 | 6102 | 3.5 | 355.95 | 2425 | 250 | 103.0928 | 3.4 | 18 | 0.83 | 163 | 9 | 375 | 31.9 | 246 | 7 | 7.94
2025-11-21 | 10031 | 60 | 6018.6 | 3.4 | 341.054 | 2420 | 260 | 107.438 | 3.55 | 22 | 1 | 190 | 14.5 | 444 | 43 | 254 | 10 | 7.9
2025-11-22 | 12670 | 60 | 7602 | 3.4 | 430.78 | 2413 | 260 | 107.7497 | 3.5 | 23 | 0.73 | 153 | 14.7 | 395 | 43 | 250 | 10 | 7.92
2025-11-23 | 9794 | 60 | 5876.4 | 3.5 | 342.79 | 2433 | 246 | 101.1097 | 3.1 | 21 | 0.48 | 156 | 12 | 385 | 29.6 | 247 | 8 | 7.87
2025-11-24 | 10044 | 60 | 6026.4 | 3.4 | 341.496 | 2422 | 242 | 99.9174 | 3.72 | 20 | 0.86 | 138 | 8.4 | 393 | 27.7 | 253 | 7 | 7.95
2025-11-25 | 10105 | 60 | 6063 | 3.4 | 343.57 | 2420 | 255 | 105.3719 | 3.3 | 18 | 0.78 | 155 | 12 | 392 | 31 | 251 | 9 | 7.9
2025-11-26 | 10152 | 60 | 6091.2 | 3.6 | 365.472 | 2427 | 235 | 96.8274 | 3 | 18 | 0.81 | 142 | 7.6 | 500 | 25 | 248 | 6 | 7.91
2025-11-27 | 10154 | 60 | 6092.4 | 3.3 | 335.082 | 2397 | 263 | 109.7205 | 3.8 | 21 | 0.78 | 121 | 11 | 490 | 38.6 | 252 | 8.1 | 7.86
2025-11-28 | 10282 | 60 | 6169.2 | 3.5 | 359.87 | 2387 | 237 | 99.2878 | 3.2 | 18 | 0.44 | 120 | 7.7 | 450 | 29 | 246 | 7 | 7.93
2025-11-29 | 10169 | 60 | 6101.4 | 3.6 | 366.084 | 2386 | 257 | 107.7117 | 3.5 | 18 | 0.72 | 164 | 14 | 500 | 37 | 250 | 9 | 7.9
2025-11-30 | 10044 | 64 | 6428.16 | 3.6 | 361.584 | 2365 | 238 | 100.6342 | 3.3 | 21 | 0.34 | 123 | 15 | 470 | 38 | 254 | 10.1 | 7.92
2025-12-01 | 10567 | 64 | 6762.88 | 3.4 | 359.278 | 2385 | 251 | 105.2411 | 3.74 | 18.6 | 0.82 | 140 | 12.7 | 500 | 37 | 249 | 9 | 7.87
2025-12-02 | 12875 | 64 | 8240 | 3.3 | 424.875 | 2367 | 271 | 114.4909 | 3 | 19 | 0.81 | 180 | 15 | 480 | 37 | 251 | 11 | 7.94
2025-12-03 | 10668 | 64 | 6827.52 | 3.5 | 373.38 | 2363 | 271 | 114.6847 | 3.6 | 19 | 0.41 | 177 | 14 | 540 | 37 | 221 | 9.2 | 7.9
2025-12-04 | 10268 | 64 | 6571.52 | 3.5 | 359.38 | 2374 | 263 | 110.7835 | 3.35 | 17 | 0.78 | 188 | 13 | 460 | 38 | 253 | 8.3 | 7.91
2025-12-05 | 10668 | 64 | 6827.52 | 3.6 | 384.048 | 2366 | 258 | 109.0448 | 3.8 | 19 | 0.56 | 160 | 12 | 500 | 39 | 248 | 8.6 | 7.88
2025-12-06 | 10168 | 64 | 6507.52 | 3.6 | 366.048 | 2369 | 244 | 102.997 | 3 | 19 | 0.46 | 138 | 11 | 530 | 35 | 252 | 9.3 | 7.6
2025-12-07 | 10157 | 64 | 6500.48 | 3.4 | 345.338 | 2394 | 239 | 99.8329 | 3.6 | 18 | 0.77 | 150 | 9.6 | 540 | 22.2 | 246 | 8 | 7.54
2025-12-08 | 10295 | 64 | 6588.8 | 3.3 | 339.735 | 2376 | 235 | 98.9057 | 3.32 | 18 | 0.41 | 140 | 9.5 | 490 | 31 | 200 | 8 | 7.63
2025-12-09 | 10166 | 64 | 6506.24 | 3.5 | 355.81 | 2395 | 270 | 112.7349 | 3.5 | 19 | 0.28 | 130 | 16 | 539 | 43 | 249 | 10 | 7.6
2025-12-10 | 10291 | 64 | 6586.24 | 3.5 | 360.185 | 2368 | 253 | 106.8412 | 3.3 | 19 | 0.39 | 140 | 12.6 | 489 | 37.9 | 254 | 9 | 7.62
2025-12-11 | 10641 | 64 | 6810.24 | 3.5 | 372.435 | 2375 | 245 | 103.1579 | 3.45 | 16 | 0.48 | 124 | 12 | 500 | 41 | 247 | 8.7 | 7.57
2025-12-12 | 10164 | 64 | 6504.96 | 3.4 | 345.576 | 2391 | 243 | 101.6311 | 3.8 | 16 | 0.81 | 130 | 13 | 500 | 30 | 250 | 10 | 7.64
2025-12-13 | 10164 | 64 | 6504.96 | 3.4 | 345.576 | 2393 | 261 | 109.0681 | 3.4 | 19 | 0.88 | 190 | 14 | 480 | 37.1 | 253 | 10 | 7.6
2025-12-14 | 10100 | 64 | 6464 | 3.6 | 363.6 | 2363 | 267 | 112.992 | 4.02 | 17 | 0.45 | 178 | 16.4 | 530 | 46.1 | 245 | 9.7 | 7.61
2025-12-15 | 10547 | 64 | 6750.08 | 3.3 | 348.051 | 2398 | 269 | 112.1768 | 3.6 | 19 | 0.67 | 170 | 16 | 400 | 38 | 251 | 10 | 7.57
2025-12-16 | 10032 | 64 | 6420.48 | 3.5 | 351.12 | 2390 | 266 | 111.2971 | 3.3 | 16 | 0.52 | 156 | 15 | 530 | 46 | 248 | 10 | 7.63
2025-12-17 | 10100 | 64 | 6464 | 3.6 | 363.6 | 2364 | 268 | 113.3672 | 4.1 | 16 | 0.89 | 157 | 14.8 | 540 | 42 | 252 | 11 | 7.6
2025-12-18 | 10470 | 63 | 6596.1 | 3.6 | 376.92 | 2383 | 236 | 99.0348 | 3.5 | 18 | 0.61 | 150 | 11.2 | 396 | 37 | 246 | 8 | 7.62
2025-12-19 | 10162 | 63 | 6402.06 | 3.4 | 345.508 | 2368 | 260 | 109.7973 | 3.8 | 16.5 | 0.86 | 155 | 12 | 411 | 28 | 167 | 9.7 | 7.56
2025-12-20 | 10060 | 63 | 6337.8 | 3.3 | 331.98 | 2396 | 255 | 106.4274 | 3.6 | 17 | 0.34 | 123 | 11.8 | 417 | 37.7 | 250 | 10.3 | 7.64
2025-12-21 | 10605 | 63 | 6681.15 | 3.5 | 371.175 | 2385 | 245 | 102.7254 | 4.04 | 17 | 0.88 | 123 | 7 | 290 | 29 | 164 | 6 | 7.6
2025-12-22 | 2562 | 63 | 1614.06 | 3.5 | 89.67 | 2393 | 264 | 110.3218 | 3.3 | 16 | 0.38 | 160 | 14 | 415 | 40 | 253 | 10 | 7.61
2025-12-23 | 8782 | 63 | 5532.66 | 3.5 | 307.37 | 2395 | 260 | 108.5595 | 3.9 | 18 | 0.88 | 139 | 12 | 410 | 36 | 251 | 9 | 7.58
2025-12-24 | 12657 | 63 | 7973.91 | 3.4 | 430.338 | 2363 | 242 | 102.4122 | 3.65 | 19 | 0.44 | 157 | 13 | 421 | 38 | 248 | 9 | 8.1
2025-12-25 | 10682 | 63 | 6729.66 | 3.4 | 363.188 | 2371 | 266 | 112.1889 | 4.1 | 17 | 0.34 | 137 | 12 | 395 | 32 | 252 | 9.6 | 8.04
2025-12-26 | 9794 | 63 | 6170.22 | 3.3 | 323.202 | 2399 | 259 | 107.9617 | 3.3 | 17 | 0.54 | 136 | 12 | 411 | 34.7 | 246 | 10 | 8.13
2025-12-27 | 9806 | 63 | 6177.78 | 3.5 | 343.21 | 2473 | 252 | 101.9005 | 3.9 | 19 | 0.73 | 134 | 10 | 404 | 31 | 180 | 7 | 8.1
2025-12-28 | 10300 | 63 | 6489 | 3.5 | 360.5 | 2457 | 248 | 100.9361 | 3.62 | 17.8 | 0.77 | 139 | 11.7 | 415 | 36 | 254 | 8.9 | 8.12
2025-12-29 | 10041 | 63 | 6325.83 | 3.5 | 351.435 | 2485 | 276 | 111.0664 | 3.8 | 19 | 0.65 | 166 | 15 | 405 | 40 | 249 | 11 | 8.07
2025-12-30 | 10100 | 63 | 6363 | 3.4 | 343.4 | 2466 | 263 | 106.6504 | 3.6 | 17 | 0.59 | 163 | 14 | 417 | 35.4 | 251 | 11 | 8.15
2025-12-31 | 10640 | 63 | 6703.2 | 3.4 | 361.76 | 2355 | 251 | 106.5817 | 4 | 18 | 0.53 | 140 | 14 | 403 | 39 | 255 | 12 | 8.2
[9 empty] | التاريخ | درجة الحرارة

## plant information
General Information
Parameter | Value | Unit
WWTP name | Karbala WWTP | _
process | Conventional Activated Sludge | _
Number of clarifiers | 8 | _
Clarifier type | circular | _
Design Parameters
Parameter | Value | Unit
Diameter | 32 | m
Side Water Depth | 4 | m
Center Depth | 5.15 | m
Bottom Slope | 1:12 | -
Feed Pipe Diameter | 0.8 | m
Calculated Design Parameters
Parameter | Value | unit
Surface Area (one tank ) | 804 | m2
Total Surface Area | 6432 | m2
Operational volume (one tanke) | 3216 | m3
Total Volume | 25728 | m3
Surface Area calculated using A=π/4 *d2
Operational Volume calculated using SWD = 4.0 m
Center Depth is provided for reference only

## Calculation
Solid loding Rate SLR (Kg/m2*h) | Surface Overflow Rate SOR (m3/m2*d) | hydraulic retention time HRT (h) | % TSS removal | % COD removal | % BOD removal
1.6966 | 14.0211 | 4.2793 | 92.1429 | 90.2 | 96
1.7106 | 14.0211 | 4.2793 | 92.3077 | 93.75 | 96.8548
1.7134 | 14.0522 | 4.2698 | 94.5522 | 92.875 | 97.6285
1.7062 | 14.0697 | 4.2645 | 91 | 91.6 | 96.0159
1.6976 | 14.0373 | 4.2743 | 90.9677 | 90.6158 | 96.1382
1.7166 | 14.0473 | 4.2713 | 95.625 | 95.1389 | 96
1.7247 | 14.1604 | 4.2372 | 91.5254 | 92.1 | 96.506
1.738 | 14.1915 | 4.2279 | 90.9722 | 92.78 | 96.0317
1.7762 | 14.5348 | 4.128 | 91.2338 | 92.6923 | 96.5667
1.7678 | 14.4353 | 4.1565 | 94.7059 | 95.1852 | 96.8
1.7714 | 14.4254 | 4.1593 | 94.3704 | 93.1818 | 95.8333
1.7427 | 14.4266 | 4.159 | 92.6446 | 92 | 96.898
1.7927 | 14.5908 | 4.1122 | 94.7904 | 93.3023 | 95.7143
1.7631 | 14.5311 | 4.1291 | 91.5625 | 87.9429 | 95.8871
1.7745 | 14.7463 | 4.0688 | 92.0732 | 91.5217 | 96.7742
1.7673 | 14.6866 | 4.0854 | 93.4307 | 94.6735 | 96.748
1.7782 | 14.7363 | 4.0716 | 91.0714 | 91.4 | 96.1417
1.7873 | 14.7624 | 4.1158 | 91.6667 | 93.0233 | 97.2
1.7623 | 14.7488 | 4.1196 | 90.0763 | 92 | 96.7611
1.7563 | 14.7313 | 4.1245 | 94.5833 | 94 | 97.5494
1.7765 | 14.6654 | 4.143 | 90.1639 | 93.5272 | 97.3333
1.7598 | 14.6393 | 4.1504 | 90.0398 | 93.5849 | 96.1923
1.756 | 14.704 | 4.1322 | 95.5625 | 94.3396 | 97.3016
1.771 | 14.6517 | 4.1469 | 92 | 93.6735 | 97.2764
1.7474 | 14.6729 | 4.1409 | 94.3548 | 95.28 | 93.6
1.7774 | 14.7052 | 4.1318 | 92.3729 | 94.8333 | 95.3947
1.7731 | 14.8308 | 4.0968 | 92.9134 | 93.1868 | 96.9478
1.7919 | 14.8246 | 4.0986 | 92.5 | 92.1739 | 96.5339
1.7866 | 14.8296 | 4.0972 | 94.5455 | 92.8935 | 97.166
1.8059 | 14.9813 | 4.0557 | 92.5 | 94.3636 | 97.3123
1.5495 | 13.2152 | 4.5977 | 90.7692 | 91.42 | 96.371
1.4163 | 12.1269 | 5.0103 | 90.4 | 93.26 | 96.4286
2.2243 | 18.7077 | 3.2478 | 91.1392 | 92.9254 | 95.935
2.2232 | 18.7612 | 3.2386 | 92.9688 | 94.4043 | 93.9091
2.209 | 18.8085 | 3.2304 | 90.5797 | 89.4595 | 96.2249
2.3037 | 19.4838 | 3.1185 | 90.9774 | 91.6596 | 96.063
2.3219 | 19.5398 | 3.1095 | 92.5556 | 92.7692 | 96.3563
2.3885 | 20.2575 | 2.9994 | 92 | 92.7698 | 95.88
2.3849 | 20.3632 | 2.9838 | 92.6667 | 93.4717 | 96.2846
2.4336 | 20.6978 | 2.9356 | 93.1818 | 91.9149 | 96.1224
2.4345 | 20.74 | 2.9296 | 92.9412 | 91.6 | 96.5737
2.418 | 20.4055 | 2.9776 | 94.0645 | 93.3333 | 97.0968
2.3859 | 20.4751 | 2.9675 | 93.2143 | 94.44 | 96.8651
2.3958 | 20.3644 | 2.9836 | 91.5344 | 90.4348 | 95.9756
2.2791 | 20.3644 | 2.9836 | 93.1579 | 92.48 | 96.811
2.3787 | 20.1182 | 3.0201 | 93.2143 | 93.1111 | 96.44
2.3695 | 20.1642 | 3.0132 | 89.3939 | 90.1628 | 95.5466
2.3402 | 19.959 | 3.0442 | 91.1765 | 92.3404 | 96.4427
2.3277 | 19.9764 | 3.0416 | 93.2331 | 91.7949 | 96.8127
2.3117 | 19.6281 | 3.0955 | 92.126 | 93.6694 | 96.8952
2.2012 | 19.6455 | 3.0928 | 93.3333 | 93.9623 | 95.8333
2.3245 | 19.5398 | 3.1095 | 92.1053 | 92.0956 | 95.5285
2.2869 | 19.505 | 3.1151 | 95.102 | 95.75 | 97.6
2.2536 | 19.199 | 3.1647 | 92.4731 | 92.2449 | 96.1811
2.2931 | 19.2761 | 3.1521 | 91.0569 | 92.7928 | 97.1888
2.2377 | 18.852 | 3.223 | 94.2857 | 93.4763 | 97.2112
1.4771 | 12.5 | 4.8608 | 91.4286 | 92.349 | 96.7611
2.2092 | 18.6953 | 3.25 | 91.3386 | 91.4254 | 96.4427
2.1872 | 18.7177 | 3.2461 | 94.2675 | 94.0411 | 96.5323
2.204 | 18.5784 | 3.2704 | 92 | 91.3034 | 96.4286
2.3708 | 18.592 | 3.268 | 90.7692 | 93.1935 | 96.8293
2.3955 | 18.7177 | 3.2461 | 93.007 | 93.1034 | 96.8127
2.3556 | 18.5784 | 3.2704 | 91.3333 | 91.4607 | 96.3855
2.3647 | 18.592 | 3.268 | 94.7879 | 93.0365 | 96.6535
2.3727 | 18.7612 | 3.2386 | 91.6667 | 92.46 | 97.2065
2.5761 | 19.2761 | 3.1521 | 99.1806 | 92.6991 | 96.8
2.3817 | 18.852 | 3.223 | 93 | 91.3667 | 96.4822
2.511 | 19.5398 | 3.1095 | 92.75 | 91.3093 | 96.5714
2.5979 | 20.2575 | 2.9994 | 94.8 | 93.0465 | 97.1315
2.5685 | 20.3632 | 2.9838 | 94.2308 | 94.4934 | 97.1774
2.4917 | 19.5398 | 3.1095 | 93.7888 | 93.9597 | 97.3016
2.5912 | 20.2575 | 2.9994 | 91.5033 | 93.8889 | 96.4634
2.5739 | 20.3632 | 2.9838 | 95.1724 | 95.9444 | 97.5591
2.6407 | 20.74 | 2.9296 | 94.1935 | 94.2593 | 97.2
2.6155 | 20.4055 | 2.9776 | 90.1481 | 92.963 | 96.3563
2.6177 | 20.4751 | 2.9675 | 95 | 94.3396 | 97.3913
2.5674 | 20.3644 | 2.9836 | 90.5 | 92.6531 | 96.0159
2.621 | 20.3644 | 2.9836 | 92 | 93.3704 | 95.9677
2.5902 | 20.4067 | 2.9774 | 92.2078 | 92.6 | 96.627
2.6093 | 20.4092 | 2.9771 | 94.1176 | 93.475 | 97.561
2.5684 | 20.3197 | 2.9902 | 93.4375 | 93.102 | 97.16
2.5597 | 20.209 | 3.0066 | 94.183 | 95.0909 | 96.8898
2.5728 | 20.1132 | 3.0209 | 94.1176 | 94.4 | 96.7871
2.4971 | 19.4913 | 3.1173 | 95.2439 | 93.65 | 97.5697
2.406 | 19.0249 | 3.1937 | 92.4837 | 91.8919 | 96.6397
2.4022 | 18.8085 | 3.2304 | 91.7241 | 91.8 | 96.3241
2.6903 | 18.5585 | 3.274 | 94.8387 | 95.1852 | 97.0161
2.3512 | 18.4478 | 3.2936 | 95.5601 | 94.8511 | 97.5794
2.2757 | 18.0323 | 3.3695 | 93.0556 | 93.8889 | 96.5854
2.1689 | 17.1592 | 3.5409 | 95.2381 | 95 | 97.8088
2.1978 | 16.7425 | 3.629 | 93.2143 | 90.5983 | 97.1084
2.1711 | 16.3744 | 3.7106 | 93.3333 | 91.6279 | 97.0472
2.0711 | 15.7537 | 3.8568 | 93.2716 | 90.9884 | 96.3563
2.1111 | 15.8047 | 3.8444 | 94 | 91.7898 | 96.8
2.0651 | 15.7002 | 3.87 | 94.4444 | 93.75 | 97.5099
2.4957 | 15.6007 | 3.8947 | 94.3548 | 93.8838 | 97.3878
2.0691 | 15.4975 | 3.9206 | 92.2619 | 90.7246 | 96.8127
2.032 | 15.4403 | 3.9351 | 93.4 | 91.6208 | 97.1774
2.078 | 15.2985 | 3.8498 | 92.3529 | 93 | 96
2.0167 | 15.2935 | 3.9729 | 91.8699 | 91.5152 | 96.748
2.0178 | 15.1057 | 4.0223 | 92.4324 | 91.4091 | 96.063
2.0086 | 15.1343 | 4.0147 | 92 | 91.3874 | 96.04
1.9752 | 14.8234 | 4.0989 | 93.9041 | 91.4769 | 97.166
1.9527 | 14.8234 | 4.0989 | 92.1212 | 90.7787 | 95.6522
2.0002 | 15.1306 | 4.0157 | 92.8777 | 93.1 | 96.5737
1.9857 | 15.1343 | 4.0147 | 93.8608 | 91.404 | 96.7742
1.9538 | 14.5448 | 4.1252 | 92.7692 | 92.0118 | 96.8254
1.9475 | 14.5336 | 4.1284 | 93.6735 | 91.5134 | 96.4634
1.9946 | 14.8706 | 4.0348 | 94.375 | 93.4959 | 97.08
2.0015 | 14.8184 | 4.049 | 92.3188 | 94.5073 | 96.6929
1.9285 | 14.342 | 4.1835 | 92.1311 | 93.3884 | 97.1888
1.8593 | 14.0149 | 4.2812 | 93.0597 | 93.4335 | 97.0916
1.8822 | 14.046 | 4.2717 | 93.8889 | 93.5343 | 96.7611
1.934 | 14.3756 | 4.1737 | 92.5926 | 94.5833 | 96.8379
1.9172 | 14.2015 | 4.2249 | 92.2619 | 92.0085 | 95.5645
1.8718 | 14.0522 | 4.2698 | 90.5512 | 92.8694 | 96.1508
1.8686 | 14.0498 | 4.2705 | 92.9936 | 92.766 | 96.7073
1.945 | 14.4789 | 4.144 | 94.2675 | 94.0447 | 96.8127
1.9166 | 14.3532 | 4.1802 | 92.2222 | 90.7598 | 95.5823
1.9262 | 14.3744 | 4.1741 | 92.5175 | 93.57 | 96.6535
1.8155 | 13.908 | 4.3141 | 92.9333 | 94.058 | 96.6397
1.8079 | 13.893 | 4.3187 | 92.8485 | 92.9006 | 96.72
1.8789 | 14.4826 | 4.1429 | 91.5278 | 92.4638 | 95.8103
1.8881 | 14.5609 | 4.1206 | 92.7407 | 92.4895 | 97.1429
1.9089 | 14.5348 | 4.128 | 92 | 92.7195 | 96.8127
1.8984 | 14.3744 | 4.1741 | 92.3571 | 92.887 | 96.6935
1.8708 | 14.4055 | 4.1651 | 92.6452 | 92.0245 | 96.3095
1.9265 | 14.6393 | 4.0986 | 92.9348 | 91.75 | 96.1382
1.9376 | 14.6866 | 4.0854 | 94.3169 | 90.3571 | 96.4961
1.8646 | 14.2189 | 4.2197 | 92.7381 | 93.133 | 96.4
1.855 | 14.24 | 4.2135 | 92.3077 | 92.4948 | 96.3563
1.8293 | 14.0286 | 4.277 | 91.7284 | 91.75 | 96.7194
1.851 | 14.1157 | 4.2506 | 90.4762 | 91.7127 | 96.1481
1.8717 | 14.3607 | 4.1781 | 92.8235 | 92.2737 | 96.371
1.9168 | 14.6393 | 4.0986 | 93.1977 | 90.9006 | 96.0317
1.8829 | 14.4838 | 4.1426 | 93.7107 | 91.5408 | 96.2963
1.9399 | 14.8234 | 4.0477 | 92.9375 | 93.5543 | 96.4
1.8947 | 14.3607 | 4.1781 | 92.1528 | 92.9119 | 96.6535
1.9 | 14.3794 | 4.1726 | 92.2069 | 91.6189 | 96.7871
1.875 | 14.2189 | 4.2197 | 93.1548 | 91.08 | 96.8127
1.8774 | 14.2873 | 4.1995 | 93.5329 | 91.9431 | 96.7611
1.8586 | 14.0945 | 4.257 | 92.0261 | 93.0435 | 96.8379
1.8246 | 14.0498 | 4.2705 | 93.0357 | 91.1475 | 97.1774
1.9087 | 14.5336 | 4.1284 | 93.2317 | 92.766 | 95.9921
1.8931 | 14.5473 | 4.1245 | 92.9878 | 91.3408 | 97.1545
1.8577 | 14.1517 | 4.2398 | 91.9444 | 90.4082 | 96.4143
1.8104 | 13.8905 | 4.3195 | 89.8693 | 91.6667 | 95.5823
1.8368 | 13.8943 | 4.3183 | 93.4831 | 92.887 | 96.8504
1.8714 | 14.199 | 4.2256 | 92.378 | 92.4812 | 96.3563
1.8674 | 14.2189 | 4.2197 | 91.4286 | 92.2086 | 96.8
2.055 | 14.2711 | 4.2043 | 93.6612 | 92.093 | 96.4427
2.0017 | 14.0174 | 4.2804 | 93.1792 | 93.018 | 96.3265
1.9979 | 13.9129 | 4.3125 | 93.4197 | 93.018 | 95.6972
1.9979 | 14.0634 | 4.2664 | 91.2963 | 92.0335 | 95.8468
2.0014 | 14.0808 | 4.2611 | 92.0994 | 91.5745 | 94.8413
2.0241 | 14.0498 | 4.2705 | 91.4368 | 90.54 | 95.5285
1.9771 | 13.8905 | 4.3195 | 94.1358 | 92.8837 | 93.2039
1.9943 | 13.8943 | 4.3183 | 94.8454 | 90.1961 | 96.4
1.9629 | 13.7264 | 4.3711 | 93.0366 | 91 | 95.9514
2.0038 | 14.0323 | 4.2758 | 91.5341 | 90.4639 | 96.0474
2.0163 | 14.0348 | 4.2751 | 90.9942 | 90.1515 | 96.0558
1.9656 | 13.7388 | 4.3672 | 92.4211 | 90.1579 | 96.7742
1.9766 | 13.7388 | 4.3672 | 92.1466 | 90 | 96.4683
2.066 | 14.3607 | 4.1781 | 92.3077 | 91.5 | 95.935
2.0651 | 14.3607 | 4.1781 | 92.1978 | 90.4393 | 96
2.012 | 14.0634 | 4.2664 | 94.6524 | 90.6667 | 96.8504
2.0307 | 14.0498 | 4.2705 | 94.8913 | 91.3158 | 96.7871
1.9767 | 13.8943 | 4.3183 | 91.6667 | 90.25 | 96.4143
1.9449 | 13.5883 | 4.4156 | 92.5466 | 91.7619 | 96.3563
1.9683 | 13.6182 | 4.4059 | 91.6667 | 91.3636 | 95.8103
1.9145 | 13.4254 | 4.4691 | 92.9039 | 92.7083 | 96.7742
1.932 | 13.4415 | 4.4638 | 91.6763 | 90.3256 | 95.6349
1.9696 | 13.6654 | 4.3906 | 91.1176 | 90.7442 | 95.8943
1.9698 | 13.6791 | 4.3863 | 92.3404 | 90.7692 | 95.8964
2.0232 | 14.0498 | 4.2705 | 95.3939 | 92.7333 | 95.7143
1.9298 | 13.5771 | 4.4192 | 92.2857 | 90 | 96.4567
2.0139 | 14.0634 | 4.2664 | 91.5663 | 89.2857 | 95.7085
2.0209 | 14.2052 | 4.2238 | 92.6136 | 90.0526 | 96.24
2.0515 | 14.24 | 4.2135 | 95.0521 | 90.6875 | 97.3913
2.0345 | 14.0634 | 4.2664 | 92.1765 | 91.3778 | 95.9184
1.9281 | 13.7525 | 4.3628 | 91.3889 | 90.2703 | 94.6614
1.8932 | 13.7388 | 4.3672 | 92.8426 | 89.3651 | 96.0081
1.879 | 13.4279 | 4.4683 | 90.5882 | 89.7297 | 96.0317
1.906 | 13.7388 | 4.3672 | 94.2683 | 90.3955 | 96.626
1.9277 | 13.7562 | 4.3617 | 94.8148 | 88.1481 | 97.0866
1.8772 | 13.5833 | 4.4172 | 91.8182 | 90.3191 | 94.4
1.8945 | 13.597 | 4.4127 | 90.8824 | 92.449 | 95.5466
1.8424 | 13.255 | 4.5266 | 92.0812 | 90 | 95.2569
1.8564 | 13.2724 | 4.5207 | 92.8351 | 90.5278 | 95.7371
1.9052 | 13.7525 | 4.3628 | 91.4835 | 90.4348 | 95.4435
1.9228 | 13.7736 | 4.3561 | 91.8717 | 90 | 95.5952
1.8581 | 13.4254 | 4.4691 | 91.4118 | 87.8788 | 95.5285
1.8541 | 13.4291 | 4.4679 | 92.4211 | 90.7583 | 95.56
1.821 | 13.1828 | 4.5514 | 91.7436 | 91.8519 | 94.8819
1.8189 | 13.1169 | 4.5742 | 90.6707 | 85.098 | 95.3414
1.8618 | 13.2861 | 4.516 | 91.4286 | 89.7778 | 96.1753
1.8388 | 13.2351 | 4.5334 | 91.3793 | 87.2434 | 95.83
1.8617 | 13.2724 | 4.5207 | 94.6429 | 91.8605 | 96.8379
1.8991 | 13.5846 | 4.4168 | 92.5521 | 89.0055 | 96.2903
1.8728 | 13.597 | 4.4127 | 94.5355 | 91.3889 | 97.1825
1.836 | 13.2662 | 4.5228 | 91.7368 | 87.8453 | 96.3415
1.8511 | 13.2662 | 4.5228 | 92.4324 | 87.4286 | 96.3745
1.8609 | 13.2861 | 4.516 | 92.5 | 88.5246 | 95.5823
1.8746 | 13.597 | 4.4127 | 91.1111 | 87.1429 | 96.0236
1.8958 | 13.6654 | 4.3906 | 92.25 | 90.3047 | 95.5466
1.8491 | 13.2711 | 4.5211 | 92.3669 | 89.8901 | 96.2
1.8538 | 13.2861 | 4.516 | 91.1515 | 89.375 | 95.6917
1.8358 | 13.2711 | 4.5211 | 91.8129 | 90.411 | 96.4082
1.8423 | 13.2861 | 4.516 | 92.1875 | 89.4444 | 96.4143
1.8387 | 13.2662 | 4.5228 | 91.6279 | 88.5965 | 96.129
1.9725 | 13.2861 | 4.516 | 91.5135 | 90.0217 | 95.6349
2.0547 | 13.2711 | 4.3841 | 90.9836 | 88.4118 | 96.3415
1.9606 | 12.6468 | 4.6005 | 95.4315 | 93.0788 | 96.8504
2.036 | 13.2861 | 4.3792 | 92.1667 | 91.1215 | 96.4
2.0365 | 13.2711 | 4.3841 | 92.5 | 90.7143 | 96.7611
2.0506 | 13.2861 | 4.3792 | 94.0828 | 91.5663 | 97.2332
2.0591 | 13.3172 | 4.3689 | 90.9697 | 90.0922 | 96.0159
2.0424 | 13.2861 | 4.3792 | 93.5057 | 91.0441 | 96.9355
2.026 | 13.2687 | 4.3849 | 92.0115 | 91.1628 | 96.0317
1.932 | 12.6468 | 4.6005 | 94.5652 | 92.9657 | 96.1039
2.1711 | 14.2189 | 4.0919 | 92.4064 | 90.4433 | 96
2.2153 | 14.3595 | 4.0518 | 92.6136 | 90.6618 | 96.063
2.1899 | 14.3744 | 4.0476 | 94.2045 | 92.5926 | 96.8675
2.2203 | 14.5149 | 4.0084 | 91.3772 | 91.5888 | 96.0956
2.2187 | 14.5435 | 4.0005 | 92.0213 | 89.6806 | 95.7895
2.1906 | 14.1679 | 4.1066 | 92.6344 | 90.6635 | 96.0474
2.2527 | 14.6343 | 3.9757 | 90.9146 | 87.715 | 95.5645
2.2845 | 14.8408 | 3.9204 | 90.9524 | 88.5714 | 96.4286
2.2913 | 14.8259 | 3.9243 | 92.0588 | 91.8224 | 95.935
2.2834 | 14.8408 | 3.9204 | 92.0245 | 92 | 95.6175
2.4873 | 16.1007 | 3.6136 | 92.2162 | 88.3333 | 96.3855
2.4167 | 15.7562 | 3.6926 | 93.0928 | 91 | 96.6535
2.4213 | 15.8358 | 3.6741 | 91.4201 | 87.9412 | 96.3968
2.4756 | 16.0896 | 3.6161 | 91.9075 | 91.2088 | 94.8
2.4541 | 16.1157 | 3.6103 | 93.2653 | 90.5405 | 96.4427
2.4964 | 16.2251 | 3.5859 | 92.8422 | 90.2162 | 96.3265
2.463 | 16.1157 | 3.6103 | 92.6738 | 89.6667 | 95.7371
2.4097 | 16.1007 | 3.7265 | 94.6296 | 92.6316 | 97.5806
2.3692 | 15.9291 | 3.7667 | 95.2 | 94.9811 | 96.8254
2.3748 | 16.0535 | 3.7375 | 91.0241 | 90.9091 | 94.7154
2.4615 | 16.0535 | 3.7375 | 91.6959 | 88.8037 | 96.4567
2.4018 | 15.7736 | 3.8038 | 91.875 | 90.2093 | 96
2.4957 | 16.2201 | 3.6991 | 92.5926 | 87.594 | 95.8704
2.4144 | 15.7873 | 3.8005 | 92.4051 | 90.6563 | 96.4427
2.4197 | 15.7736 | 3.8038 | 93.4426 | 85.7333 | 96.2151
2.4657 | 16.1157 | 3.7231 | 91.9108 | 93.1915 | 96.25
2.4965 | 16.2251 | 3.698 | 93.75 | 93.8636 | 96.5476
2.4431 | 16.1157 | 3.7231 | 92.7381 | 90 | 96.3415
2.4455 | 16.0535 | 3.7375 | 91.9632 | 94.186 | 96.44
2.4663 | 16.0846 | 3.7303 | 93.8122 | 91.0909 | 96.2598
2.4591 | 16.1007 | 3.7265 | 90.6494 | 88.1818 | 95.743
2.4202 | 15.9291 | 3.7667 | 92.4224 | 90.0541 | 96.3745
2.4605 | 16.0535 | 3.7375 | 91.7262 | 90 | 96.6397
2.454 | 16.0535 | 3.7375 | 92.2353 | 89.697 | 96.8379
2.4412 | 16.0535 | 3.7375 | 90.1961 | 88.1471 | 95.9677
2.4 | 15.8035 | 3.7966 | 92.7222 | 89.1351 | 96.4286
2.4464 | 16.0522 | 3.7378 | 91.4865 | 90.2564 | 95.935
2.4635 | 16.0522 | 3.7378 | 92.6627 | 89.3939 | 93
2.4626 | 16.0535 | 3.7375 | 92.2414 | 88.8235 | 95.9839
2.5512 | 15.9129 | 3.6125 | 93.2749 | 92.675 | 96.4567
2.536 | 15.9291 | 3.6088 | 91.8675 | 91.3953 | 95.7085
2.5999 | 16.3806 | 3.5093 | 91.2195 | 90.7143 | 95.6
2.6892 | 16.7376 | 3.4345 | 92.7374 | 90 | 96.0474
2.6447 | 16.7065 | 3.4409 | 92.426 | 89.3252 | 95.9184
2.5458 | 16.0535 | 3.5808 | 92.2289 | 88.0556 | 96.4143
2.5601 | 16.1157 | 3.567 | 90.6803 | 90.4955 | 95.6452
2.5888 | 16.2251 | 3.543 | 92.9677 | 89.4654 | 96.8254
2.5837 | 16.1157 | 3.567 | 91.6129 | 88.8372 | 96.4634
2.5402 | 16.0535 | 3.5808 | 91.8987 | 88.5093 | 96.063
2.519 | 15.7736 | 3.6444 | 91.5 | 88.3077 | 96.28
2.6586 | 16.0535 | 3.5808 | 92.2581 | 90.4399 | 95.9514
2.6418 | 16.0535 | 3.5808 | 90.6667 | 87.7134 | 96.0474
2.6351 | 16.0535 | 3.5808 | 92.3164 | 88.0878 | 96.0558
2.5725 | 15.7587 | 3.6478 | 94.5578 | 89.3558 | 97.0968
2.6108 | 15.8047 | 3.6372 | 93.2584 | 91.8 | 96.4286
2.6545 | 16.0896 | 3.5728 | 93.7427 | 89.6341 | 96.6667
2.6296 | 16.1157 | 3.567 | 93.1373 | 91.1854 | 96.8
2.5422 | 16.2251 | 3.7212 | 92.3973 | 91.25 | 96.8504
2.5336 | 16.1157 | 3.7465 | 93.4211 | 88.959 | 97.2691
2.511 | 16.0535 | 3.761 | 93.0065 | 89.8792 | 96.4143
2.4537 | 15.7736 | 3.8277 | 94.7024 | 92.7765 | 94.1667
2.5278 | 16.0522 | 3.7613 | 91.6667 | 91.7429 | 96.087
2.4767 | 15.7873 | 3.8244 | 91.5152 | 90.8511 | 95.5645
2.5563 | 16.4266 | 3.6756 | 92.5466 | 91.3953 | 96.4286
2.484 | 15.9142 | 3.7939 | 94.5355 | 93.9556 | 97.2358
2.5063 | 15.9291 | 3.7904 | 90.9091 | 91.7 | 95.8964
2.4861 | 15.9142 | 3.7939 | 92.7152 | 90.8108 | 96.3052
2.4926 | 15.9291 | 3.7904 | 93.6994 | 91.3158 | 95.6311
2.5133 | 15.9129 | 3.7942 | 94.0476 | 93.75 | 96.3158
2.4853 | 15.9428 | 3.7871 | 93.2927 | 92.8261 | 96.8
2.5021 | 15.9291 | 3.7904 | 92.9348 | 90.925 | 96.8379
2.5589 | 16.3806 | 3.6859 | 92.6761 | 92.3611 | 96
2.638 | 16.7376 | 3.6073 | 92.5287 | 90 | 95.7769
2.2123 | 14.204 | 4.2507 | 93.2787 | 93.0769 | 96.2097
2.2241 | 14.2189 | 4.2463 | 93.0822 | 92.375 | 96
2.248 | 14.3595 | 4.2047 | 94.0476 | 92.8889 | 96.748
2.2427 | 14.3744 | 4.2539 | 93.4254 | 93.2075 | 96.8504
2.2542 | 14.5149 | 4.2127 | 90.5594 | 93.1481 | 95.88
2.2462 | 14.5435 | 4.2044 | 91.6667 | 93.5417 | 96.2348
2.1845 | 14.1679 | 4.3158 | 93.4911 | 93.2 | 94.1667
2.3062 | 14.6343 | 4.1783 | 92.1687 | 89.25 | 96.0159
2.345 | 14.6853 | 4.1638 | 90 | 92.5 | 95.5645
2.0957 | 13.2711 | 4.6075 | 94.382 | 93 | 96.8254
2.1053 | 13.2711 | 4.6075 | 91.6667 | 92.0833 | 96.0569
2.0987 | 13.2898 | 4.601 | 90.9722 | 93.1734 | 95.6
2.1644 | 13.5821 | 4.502 | 93.1852 | 94.5833 | 96.3158
2.0986 | 13.3172 | 4.5916 | 92.4812 | 94 | 96.7871
2.0983 | 13.2711 | 4.6075 | 93.3566 | 92.5532 | 96.4143
2.0128 | 12.6468 | 4.835 | 90.8219 | 92.5926 | 96.2753
2.0998 | 13.2861 | 4.6023 | 91.8919 | 90.6 | 95.6522
2.1018 | 13.2711 | 4.6075 | 93.9716 | 93.52 | 97.0161
2.1025 | 13.2699 | 4.6079 | 93.5252 | 90.3727 | 94.6154
2.0944 | 13.2736 | 4.6066 | 91.7808 | 92.8497 | 96.3415
2.1893 | 13.8582 | 4.4123 | 92.4638 | 92.8511 | 97.2112
2.0195 | 12.6468 | 4.835 | 91.3514 | 90 | 95.5823
2.1559 | 13.2861 | 4.516 | 91.5254 | 90 | 96.063
2.1547 | 13.2351 | 4.5334 | 93.8849 | 92.8021 | 97.3279
2.1265 | 13.0995 | 4.5803 | 93.5821 | 93 | 97.2
2.0771 | 12.944 | 4.6353 | 93.949 | 91.0995 | 96.8379
2.1561 | 13.2711 | 4.5211 | 91.4286 | 90.75 | 95.0204
2.0508 | 12.6642 | 4.7378 | 93.8583 | 92.5253 | 97.3705
2.0749 | 12.7711 | 4.6981 | 94.8052 | 93.4837 | 97.0161
2.0592 | 12.6331 | 4.7494 | 94.4371 | 91.7436 | 96.9048
2.045 | 12.6493 | 4.7434 | 94.4785 | 91.4933 | 97.1545
2.0129 | 12.4764 | 4.8091 | 92.3684 | 90.3153 | 96.063
2.5351 | 15.7587 | 3.8074 | 90.3922 | 89.1139 | 96
1.9759 | 12.1816 | 4.9255 | 92.3077 | 92.3117 | 96.7611
2.0171 | 12.4925 | 4.8029 | 93.913 | 92.9517 | 97.2332
2.0277 | 12.5684 | 4.7739 | 92.2581 | 92.0918 | 96.4143
2.043 | 12.6269 | 4.7518 | 94.6479 | 95 | 97.5806
2.0182 | 12.6294 | 4.7508 | 90.9091 | 92.1224 | 96.7857
2.0351 | 12.7886 | 4.6917 | 93.5833 | 93.5556 | 97.1545
2.0119 | 12.648 | 4.7438 | 91.4634 | 92.6 | 96.4
2.0189 | 12.4925 | 4.6857 | 87.8049 | 91.9149 | 96.0236
2.142 | 13.143 | 4.4538 | 90.9286 | 92.6 | 96.3855
2.5901 | 16.0137 | 3.6554 | 91.6667 | 92.2917 | 95.6175
2.1425 | 13.2687 | 4.4116 | 92.0904 | 93.1481 | 95.8371
2.0718 | 12.7711 | 4.5835 | 93.0851 | 91.7391 | 96.7194
2.1452 | 13.2687 | 4.4116 | 92.5 | 92.2 | 96.5323
2.0473 | 12.6468 | 4.6286 | 92.029 | 93.3962 | 96.3095
2.0666 | 12.6331 | 4.6336 | 93.6 | 95.8889 | 96.748
2.079 | 12.8047 | 4.5715 | 93.2143 | 93.6735 | 96
2.0693 | 12.6443 | 4.6295 | 87.6923 | 92.0223 | 95.9839
2.0712 | 12.7998 | 4.5733 | 91 | 92.2495 | 96.4567
2.1479 | 13.2351 | 4.4228 | 90.3226 | 91.8 | 96.4777
2.0655 | 12.6418 | 4.6304 | 90 | 94 | 96
2.0672 | 12.6418 | 4.6304 | 92.6316 | 92.2708 | 96.0474
2.0284 | 12.5622 | 4.6597 | 90.7865 | 91.3019 | 96.0408
2.1496 | 13.1182 | 4.4623 | 90.5882 | 90.5 | 96.0159
2.0378 | 12.4776 | 4.6913 | 90.3846 | 91.3208 | 95.9677
2.0293 | 12.5622 | 4.6597 | 90.5732 | 92.2222 | 95.6349
2.1076 | 13.0224 | 4.5227 | 92.5333 | 90.6566 | 96.748
2.0327 | 12.6393 | 4.6597 | 92.2581 | 93.1873 | 94.1916
2.0361 | 12.5124 | 4.707 | 90.4065 | 90.9592 | 95.88
2.1366 | 13.1903 | 4.4651 | 94.3089 | 90 | 96.3415
0.5179 | 3.1866 | 18.4825 | 91.25 | 90.3614 | 96.0474
1.7767 | 10.9229 | 5.392 | 91.3669 | 91.2195 | 96.4143
2.5265 | 15.7425 | 3.7412 | 91.7197 | 90.9739 | 96.371
2.1395 | 13.2861 | 4.4329 | 91.2409 | 91.8987 | 96.1905
1.9848 | 12.1816 | 4.8348 | 91.1765 | 91.5572 | 95.935
2.0485 | 12.1965 | 4.8289 | 92.5373 | 92.3267 | 96.1111
2.1378 | 12.8109 | 4.5973 | 91.5827 | 91.3253 | 96.4961
2.1078 | 12.4888 | 4.7159 | 90.9639 | 90.1235 | 95.5823
2.1039 | 12.5622 | 4.6883 | 91.411 | 91.5108 | 95.6175
2.1167 | 13.2338 | 4.4504 | 90 | 90.3226 | 95.2941

## statistical analysis
Descriptive Statistics
parameter | Mean | Median | Min | Max | Std | CV
Flow | 12148.1562 | 11641 | 2562 | 16675 | 1854.6797 | 15.2672
MLSS | 2127.2219 | 2134 | 1700 | 2485 | 214.2857 | 10.0735
SVI | 101.1779 | 100.9591 | 86.0082 | 114.6847 | 6.1529 | 6.0812
DO | 3.5162 | 3.3 | 1 | 7 | 0.88027 | 25.0348
Sludge blaket | 0.59285 | 0.6 | 0.27 | 1 | 0.18842 | 31.7827
TSS Out | 11.9721 | 12 | 6 | 16.5 | 2.3892 | 19.9568
COD Out | 34.7704 | 35 | 20 | 50 | 5.6501 | 16.2497
BOD Out | 8.8877 | 9 | 5.5 | 14 | 1.4914 | 16.7801
Correlattion Matrix
| Flow | MLSS | SVI | DO | Sludge blanket | TSS Out | COD Out | BOD Out
Flow | 1 | -0.47846 | -0.21829 | -0.15451 | -0.062143 | -0.19187 | -0.16659 | -0.17721
MLSS |  | 1 | 0.22463 | 0.077417 | 0.12053 | 0.17709 | 0.13711 | 0.17567
SVI |  |  | 1 | 0.0039828 | 0.082612 | 0.63971 | 0.55177 | 0.53461
DO |  |  |  | 1 | 0.023352 | 0.094697 | 0.095231 | 0.067321
Sludge blaket |  |  |  |  | 1 | 0.069672 | 0.028109 | 0.063271
TSS Out | [5 empty] | 1 | 0.79996 | 0.80956
COD Out | [6 empty] | 1 | 0.66701
BOD Out | [7 empty] | 1

## Scientific References
Scientific References Database
No. | Category | Parameter | Symbol | Unit | Normal Range | Warning Range | Critical Range | Reference | Lower Limit | Upper Limit | Warning Lower | Warning Upper | Critical Lower | Critical Upper | Direction | Importance | Functional Area | Remarks | Data Source
1 | Effluent Quality | Effluent Total Suspended Solids | TSSe | mg/L | ≤20 mg/L | 21–30 mg/L | >30 mg/L | Metcalf & Eddy | 0 | 20 | 21 | 30 | 31 | 999 | Lower is Better | Very High | Water Quality | Indicates final effluent suspended solids quality | Laboratory
2 | Settling Performance | Sludge Volume Index | SVI | mL/g | 80–150 mL/g | 150–200 mL/g | >200 mL/g | Metcalf & Eddy | 80 | 150 | 150 | 200 | 200 | 999 | Target Range | Very High | Settling | Indicates sludge settling characteristics and bulking potential | Laboratory
3 | Sludge Management | Sludge Blanket Depth | SBD | m | ≤1.0 m | 1.0–1.5 m | >1.5 m | WEF Manual of Practice No. 11 | 0 | 1 | 1 | 1.5 | 1.5 | 999 | Lower is Better | High | Settling | Indicates sludge accumulation and clarifier storage capacity | Field Measurement
4 | Hydraulic Loading | Surface Overflow Rate | SOR | m³/m²·d | 16–28 m³/m²·day | 28–35 m³/m²·day | >35 m³/m²·day | WEF Manual of Practice No. 8 / Metcalf & Eddy | 16 | 28 | 28 | 35 | 35 | 999 | Target Range | High | Hydraulic | Indicates the hydraulic loading applied to the clarifier surface | Calculated
5 | Solids Loading | Solids Loading Rate | SLR | kg/m²·h | 4–6 kg/m²·h | 6–8 kg/m²·h | >8 kg/m²·h | Metcalf & Eddy / WEF Manual of Practice | 4 | 6 | 6 | 8 | 8 | 999 | Target Range | High | Sludge Management | Indicates the solids loading applied to the clarifier and its capacity to retain sludge without washout | Calculated
6 | Sludge Recirculation | Return Activated Sludge Ratio | RAS | % | 25–75 % | 75–100 % | >100 % | Metcalf & Eddy | 25 | 75 | 75 | 100 | 100 | 999 | Target Range | Medium | Sludge Management | Indicates the percentage of return activated sludge required to maintain stable biomass concentration | SCADA / Flow Meter
7 | Hydraulic Performance | Hydraulic Retention Time | HRT | h | 2.0–4.0 h | 1.5–2.0 h OR 4.0–5.0 h | <1.5 h OR >5.0 h | Metcalf & Eddy | 2 | 4 | 1.5 | 2 | 5 | 999 | Target Range | Medium | Hydraulic | Represents the average detention time of wastewater in the secondary clarifier. | Calculated
Laboratory
Laboratory
Field Measurement
Calculated
Calculated
SCADA / Flow Meter
Calculated

## Diagnosis
Secondary Clarifier Diagnosis System
Selected Day | 160
Parameter | Actual Value | Unit | Normal Range | Status | Severity | Possible Cause | Recommended Action | Functional Area | Priority | Last Updated | Lower Limit | Upper Limit | Warning Lower | Warning Upper | Critical Lower | Critical Upper | Direction | Parameter | Normal | Warning | Critical
Effluent Total Suspended Solids | 14.9 | mg/L | ≤20 mg/L | Normal | Low | Effluent TSS is within the target range; no significant solids carryover is indicated | Continue routine effluent quality monitoring | Water Quality | Low | 2026-09-15 | 0 | 20 | 21 | 30 | 31 | 999 | Lower is Better | TSSe | Lower is Better | Lower is Better | Lower is Better
Sludge Volume Index | 98.0392 | mL/g | 80–150 mL/g | Normal | Low | Sludge settling characteristics are within the reference range | Continue routine sludge settling monitoring | Settling | Low | 2026-09-15 | 80 | 150 | 150 | 200 | 200 | 999 | Target Range | SVI | Target Range | Target Range | Target Range
Sludge Blanket Depth | 0.41 | m | ≤1.0 m | Normal | Low | Sludge blanket accumulation is within the acceptable operating range | Continue routine sludge blanket monitoring | Sludge Management | Low | 2026-09-15 | 0 | 1 | 1 | 1.5 | 1.5 | 999 | Lower is Better | SBD | Lower is Better | Lower is Better | Lower is Better
Surface Overflow Rate | 14.0323 | m³/m²·d | 16–28 m³/m²·day | Underloaded | Low | Hydraulic loading is below the reference range; possible low influent flow or excess clarifier capacity in service | Verify influent flow and confirm the number of clarifiers in service; check whether available clarifier capacity exceeds current hydraulic demand | Hydraulic | Low | 2026-09-15 | 16 | 28 | 28 | 35 | 35 | 999 | Target Range | SOR | Target Range | Target Range | Target Range
Solids Loading Rate | 2.0038 | kg/m²·h | 4–6 kg/m²·h | Underloaded | Low | Solids loading is below the reference range; possible low influent solids load or excess clarifier capacity in service | Verify influent TSS, influent flow, RAS solids concentration and number of clarifiers in service | Solids Loading | Low | 2026-09-15 | 4 | 6 | 6 | 8 | 8 | 999 | Target Range | SLR | Target Range | Target Range | Target Range
Return Activated Sludge Ratio | 60 | % | 25–75 % | Normal | Low | RAS rate is within the reference operating range | Continue routine RAS monitoring | Sludge Management | Low | 2026-09-15 | 25 | 75 | 75 | 100 | 100 | 999 | Target Range | RAS | Target Range | Target Range | Target Range
Hydraulic Retention Time | 4.2758 | h | 2.0–4.0 h | Warning | Medium | Extended hydraulic retention time; possible low influent flow or excess effective clarifier volume in service | Verify influent flow and clarifier operating configuration | Hydraulic | Medium | 2026-09-15 | 2 | 4 | 1.5 | 2 | 5 | 999 | Target Range | HRT | Target Range | Target Range | Target Range

## Clarifier Health Index CHI
Selected Day | 160
Overall CHI Score | 97
Health Status | Excellent
Parameter | Score | Weight | Weighted Score | Status
Effluent Total Suspended Solids | 100 | 35 | 35 | Normal
Sludge Volume Index | 100 | 30 | 30 | Normal
Sludge Blanket Depth | 100 | 20 | 20 | Normal
Solids Loading Rate | 80 | 15 | 12 | Underloaded
Total |  | 100 | 97

## Clarifier Stability Index CSI
Selected Day | 160
Overall CSI Score | 69
Stability Status | Warning
Operator Interpretation | Performance fluctuation detected - Increase monitoring
Parameter | Today's Value | Day Average-7 | % CV | Stability Score | Weight | Weighted Score
Sludge Volume Index | 98.0392 | 100.2733 | 5.2751 | 80 | 35 | 28
Sludge Blanket Depth | 0.41 | 0.47286 | 22.8332 | 20 | 30 | 6
Surface Overflow Rate | 14.0323 | 13.9625 | 0.93506 | 100 | 20 | 20
Hydraulic Retention Time | 4.2758 | 4.2975 | 0.94184 | 100 | 15 | 15
Total | [5 empty] | 69

## Clarifier Risk Index CRI
Selected Day | 160
Overall CRI Score | 16.25
Risk Level | Low
Operator Recommendation | Normal operation. Continue routine monitoring.
Parameter | Risk Score | Weight | Weighted Risk | Status
Effluent Total Suspended Solids | 0 | 30 | 0 | Normal
Sludge Blanket Depth | 0 | 15 | 0 | Normal
Surface Overflow Rate | 25 | 25 | 6.25 | Underloaded
Return Activated Sludge Ratio | 0 | 10 | 0 | Normal
Hydraulic Retention Time | 50 | 20 | 10 | Warning
Total |  | 100 | 16.25

## Smart Alarm System
| Total Alarms | 3
| Critical Alarms | 0
| Warning Alarms | 3
Alarm ID | Parameter | Current Value | Status | Alarm Level | Priority | Recommended Action | Functional Area
AL001 | Effluent Total Suspended Solids | 14.9 | Normal | No Alarm | Low | Continue routine effluent quality monitoring | Water Quality
AL002 | Sludge Volume Index | 98.0392 | Normal | No Alarm | Low | Continue routine sludge settling monitoring | Settling
AL003 | Sludge Blanket Depth | 0.41 | Normal | No Alarm | Low | Continue routine sludge blanket monitoring | Sludge Management
AL004 | Surface Overflow Rate | 14.0323 | Underloaded | Warning Alarm | Low | Verify influent flow and confirm the number of clarifiers in service; check whether available clarifier capacity exceeds current hydraulic demand | Hydraulic
AL005 | Solids Loading Rate | 2.0038 | Underloaded | Warning Alarm | Low | Verify influent TSS, influent flow, RAS solids concentration and number of clarifiers in service | Solids Loading
AL006 | Return Activated Sludge Ratio | 60 | Normal | No Alarm | Low | Continue routine RAS monitoring | Sludge Management
AL007 | Hydraulic Retention Time | 4.2758 | Warning | Warning Alarm | Medium | Verify influent flow and clarifier operating configuration | Hydraulic

## Operator Scorecard
Selected Day | 160
Overall Operator Score | 83.25
Performance Rating | Good
Supervisor Recommendation | Good performance. Continue routine monitoring.
Indicator | Score | Weight | Weighted Score
Clarifier Health Index (CHI) | 97 | 40 | 38.8
Clarifier Stability Index (CSI) | 69 | 30 | 20.7
Clarifier Risk Index (CRI) | 83.75 | 20 | 16.75
Alarm Management | 70 | 10 | 7
Total |  | 100 | 83.25